## raw
EPRI Power Plant Toxics Measurement Database
2017-02-28 14:29
Copyright 2015 Electric Power Research Institute (EPRI), Inc. All rights reserved.
Electric Power Research Institute and EPRI are registered service marks of the Electric Power Research Institute, Inc. EPRI.
Stack Emissions Data
Data Sources: 2010 Utility HAPs Information Collection Request
Chemical substances containing: chlori
Coal Type: All
Selected Chemical: Chlorine (Cl2)
USGS Province: All
Boiler Type: All
Gas-Side Controls: All Controls
Data Quality: Include All
Non-Detect Data: Use detection limit
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments | Changes to Reported ICR Data | ICR Reported Data Flag | ICR Standardized Data Flag | ICR Reported Concentration | ICR Reported Units of Measure | ICR Emission Factor (lb/million Btu) | ICR Reported Data Comments | ICR Reported Run Number | ICR Submittal ID
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 | < | 349 | 0.4367 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 396987.7487 | ng/dscm | 0.00034931 | [ | M26A-1 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 | < | 365 | 0.456 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 414549.9359 | ng/dscm | 0.00036476 | [ | M26A-2 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 6440 | 17.57 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26A | 202947 | dscfm | 8.4 % moisture, 10.205475 % CO2, 8.2482563019 % O2, 279.221775 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2105 | ppmv |  |  | 1 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 6150 | 16.65 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26A | 201486 | dscfm | 8.4 % moisture, 10.185575 % CO2, 8.2729263637 % O2, 298.894075 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2060 | ppmv |  |  | 2 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 11800 | 33.03 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | EPA method 26A | 203278 | dscfm | 8.4 % moisture, 10.2312 % CO2, 8.2163649782 % O2, 287.949375 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2054 | ppmv |  |  | 3 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 193 | 0.4424 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1830212 | dscfm | 15.1 % moisture, 10.88 % CO2, 8.64 % O2, 131.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. conversion error | ADL | ADL | 0.0537 | ppmv | 0.00017 |  | 3 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 200 | 0.4596 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1803934 | dscfm | 15.4 % moisture, 10.88 % CO2, 8.62 % O2, 133 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.0645 | ppmv | 0.0002 |  | 1 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 193 | 0.4424 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1824824 | dscfm | 15.3 % moisture, 10.86 % CO2, 8.63 % O2, 132.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. conversion error | ADL | ADL | 0.0549 | ppmv | 0.00017 |  | 2 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 274 | 0.6821 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1323799 | dscfm | 14.92 % moisture, 11.3 % CO2, 7.2 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.219 | ppmv | 0.000601 |  | 1 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 | < | 143 | 0.3287 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1353712 | dscfm | 14.46 % moisture, 11.4 % CO2, 7.3 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.105] | ppmv | [<0.00029] |  | 2 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 | < | 148 | 0.341 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1329926 | dscfm | 15.06 % moisture, 10.7 % CO2, 7.9 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.104] | ppmv | [<0.00030] |  | 3 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 601 | 0.7099 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 645330.2476 | ng/dscm | 0.00060098 |  | M26A-1 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 | < | 290 | 0.3396 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 308718.7705 | ng/dscm | 0.00028962 | [ | M26A-2 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 | < | 300 | 0.3368 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 306169.7717 | ng/dscm | 0.00030048 | [ | M26A-3 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 501 | 0.5796 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 526884.0262 | ng/dscm | 0.00050054 |  | M26A-1 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 589 | 0.6809 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 619037.516 | ng/dscm | 0.00058896 |  | M26A-2 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 608 | 0.706 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 641831.7281 | ng/dscm | 0.00060838 |  | M26A-3 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 294 | 0.6759 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2784213 | dscfm | 16.6 % moisture, 11.5 % CO2, 7.5 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.179 | ppmv | 0.000533 |  | 1 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 617 | 1.418 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2704794 | dscfm | 16.7 % moisture, 11.3 % CO2, 7.5 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.21 | ppmv | 0.000617 |  | 2 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 629 | 1.445 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2738425 | dscfm | 15.6 % moisture, 11.3 % CO2, 7.6 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.218 | ppmv | 0.000629 |  | 3 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 425 | 0.977 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1442542 | dscfm | 13.2 % moisture, 9.8 % CO2, 9.6 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.102] | ppmv | [<0.000339] |  | 1 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1020 | 2.344 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1421210 | dscfm | 14.7 % moisture, 9.9 % CO2, 9.2 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.243 | ppmv | 0.000815 |  | 2 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 810 | 1.862 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1435382 | dscfm | 14.9 % moisture, 9.7 % CO2, 9.1 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.195 | ppmv | 0.000647 |  | 3 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 345 | 0.3296 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 299628.8572 | ng/dscm | 0.00034502 | Method M26A DL = Adjusted volume * (mL) * 0.05 ug/mL (lowest calibration standard) See attached detection limit calculation document. | M26A-1 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 800 | 0.7879 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 716274.3536 | ng/dscm | 0.00080023 |  | M26A-2 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 629 | 0.6326 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 575125.0851 | ng/dscm | 0.00062877 |  | M26A-3 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 271 | 0.3689 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 335401.3674 | ng/dscm | 0.00027084 | [ | M29-1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 278 | 0.378 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 343654.9829 | ng/dscm | 0.0002775 | [ | M29-2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 278 | 0.3791 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 344607.7794 | ng/dscm | 0.00027827 | [ | M29-3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 271 | 0.5438 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | EPA method 26A | 33509979 | dscfm | 10.9 % moisture, 12.922825 % CO2, 4.4300675899 % O2, 166.89105 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 678 | ppmv |  |  | 1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 278 | 0.5583 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26A | 33768324 | dscfm | 10.9 % moisture, 12.940675 % CO2, 4.4073062648 % O2, 166.671625 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 1931 | ppmv |  |  | 2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 278 | 0.5583 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26A | 33693766 | dscfm | 10.9 % moisture, 12.902275 % CO2, 4.4562209265 % O2, 167.349325 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 1390 | ppmv |  |  | 3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 293 | 0.5868 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 541963 | dscfm | 11.1 % moisture, 12.91349858 % CO2, 4.4049060321 % O2, 245.3452786 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 411 | ppmv |  |  | 1 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 284 | 0.5684 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 541225 | dscfm | 11.1 % moisture, 12.8878421 % CO2, 4.4376784094 % O2, 244.6899624 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 329 | ppmv |  |  | 2 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 296 | 0.593 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 540995 | dscfm | 11.1 % moisture, 12.88162946 % CO2, 4.4456141427 % O2, 244.9691296 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 423 | ppmv |  |  | 3 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 293 | 0.3996 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 363284.1629 | ng/dscm | 0.00029335 |  | M29-1 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 284 | 0.3839 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 349026.228 | ng/dscm | 0.00028363 |  | M29-2 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 296 | 0.4011 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 364609.2305 | ng/dscm | 0.0002963 | [ | M29-3 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2145159 | dscfm | 13.3 % moisture, 11.66 % CO2, 7.83 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0594] | ppmv | [<0.00017] | RL based on MDL | 1 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2147440 | dscfm | 13.3 % moisture, 11.67 % CO2, 7.84 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0619] | ppmv | [<0.00018] | RL based on MDL | 2 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2112096 | dscfm | 13.7 % moisture, 11.64 % CO2, 7.88 % O2, 125 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0604] | ppmv | [<0.00018] | RL based on MDL | 3 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 201 | 0.4609 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2145159 | dscfm | 13.3 % moisture, 11.66 % CO2, 7.83 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0594] | ppmv | [<0.00017] | RL based on MDL | 1 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2147440 | dscfm | 13.3 % moisture, 11.67 % CO2, 7.84 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0619] | ppmv | [<0.00018] | RL based on MDL | 2 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2112096 | dscfm | 13.7 % moisture, 11.64 % CO2, 7.88 % O2, 125 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0604] | ppmv | [<0.00018] | RL based on MDL | 3 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1926479 | dscfm | 12.5 % moisture, 11.39 % CO2, 8.08 % O2, 122.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0575] | ppmv | [<0.00017] | RL based on MDL | 1 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1923024 | dscfm | 12.9 % moisture, 11.45 % CO2, 8.01 % O2, 123.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0570] | ppmv | [<0.00017] | RL based on MDL | 2 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 160 | 0.3677 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1899892 | dscfm | 12.9 % moisture, 11.42 % CO2, 8 % O2, 124 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0561] | ppmv | [<0.00016] | RL based on MDL | 3 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1892416 | dscfm | 12.9 % moisture, 11.58 % CO2, 8.03 % O2, 123.3 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0596] | ppmv | [<0.00017] | RL based on MDL | 1 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1940845 | dscfm | 12.9 % moisture, 11.64 % CO2, 7.99 % O2, 123.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0584] | ppmv | [<0.00017] | RL based on MDL | 2 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1939495 | dscfm | 13.3 % moisture, 11.64 % CO2, 7.94 % O2, 124.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0611] | ppmv | [<0.00018] | RL based on MDL | 3 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 291 | 0.3741 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 340114.1096 | ng/dscm | 0.00029123 | [ | M26A-1 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 295 | 0.3893 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 353895.9955 | ng/dscm | 0.00029511 | [ | M26A-2 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 298 | 0.3899 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 354493.9027 | ng/dscm | 0.00029755 | [ | M26A-3 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 311 | 0.3992 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 362907.7832 | ng/dscm | 0.00031075 | [ | M26A-1 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 316 | 0.4084 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 371242.3797 | ng/dscm | 0.00031577 | [ | M26A-2 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 316 | 0.4092 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 372034.233 | ng/dscm | 0.00031644 | [ | M26A-3 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 354 | 0.4207 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 382489.1031 | ng/dscm | 0.00035362 | [ | M26A-1 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 347 | 0.4362 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 396590.2817 | ng/dscm | 0.00034657 | [ | M26A-2 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 342 | 0.4304 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 391274.2446 | ng/dscm | 0.00034192 | [ | M26A-3 | 1467