## export
EPRI Power Plant Toxics Measurement Database
2017-04-18 09:37
Copyright 2015 Electric Power Research Institute (EPRI), Inc. All rights reserved.
Electric Power Research Institute and EPRI are registered service marks of the Electric Power Research Institute, Inc. EPRI.
Stack Emissions Data
Data Sources: All
Selected chemical substances: Chlorine (Cl2)
Coal Type: All
Selected Chemical: Chlorine (Cl2)
USGS Province: All
Boiler Type: All
Gas-Side Controls: All Controls
Data Quality: Include All
Non-Detect Data: Use detection limit
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments | Changes to Reported ICR Data | ICR Reported Data Flag | ICR Standardized Data Flag | ICR Reported Concentration | ICR Reported Units of Measure | ICR Emission Factor (lb/million Btu) | ICR Reported Data Comments | ICR Reported Run Number | ICR Submittal ID
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 5 |  | 6860 | 9.046 | mg/Nm3 | Good | 1993-07-15 | EPA method 9056 | EPA method 5 and 26A | 1242000 | dscfm | 29.45 in Hg, 336 deg F, 10.5 % moisture, 14.2/4.7 %CO2/%O2 | Cl2 and/or other volatile chlorine containing compounds. Further method testing was conducted at a pilot-scale coal fired boiler to assess the validity of the Cl2 results and indicated the test results were valid. Authors recommend further testing.
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 8 |  | 3340 | 4.402 | mg/Nm3 | Good | 1993-07-19 | EPA method 9056 | EPA method 5 and 26A | 1181200 | dscfm | 29.42 in Hg, 331 deg F, 10.2 % moisture, 14.4/4.7 %CO2/%O2 | Cl2 and/or other volatile chlorine containing compounds. Further method testing was conducted at a pilot-scale coal fired boiler to assess the validity of the Cl2 results and indicated the test results were valid. Authors recommend further testing.
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 2 |  | 3680 | 4.855 | mg/Nm3 | Good | 1993-07-13 | EPA method 9056 | EPA method 5 and 26A | 1199200 | dscfm | 29.39 in Hg, 339 deg F, 10.4 % moisture, 14.2/4.7 %CO2/%O2 | Cl2 and/or other volatile chlorine containing compounds. Further method testing was conducted at a pilot-scale coal fired boiler to assess the validity of the Cl2 results and indicated the test results were valid. Authors recommend further testing.
XX-D-005 | 1990s DOE Air Toxics Studies | DOE 5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 615 | 606 | Ohio Power Company | bituminous | Eastern | Ohio and Pennsylvania, Pittsburgh #8 seam | Cell | Cardinal Station, Unit 1. ESP eff. = 99 - 99.5%. ESP A SCA = 350-370 ft2/1000 acfm. Stack test conducted during soot blowing and non-sootblowing operations. | 3 |  | 1950 | 2.125 | mg/Nm3 | Good | 1993-06-25 | EPA Method 26, ion chromatography | EPA method 26 | 37247 | dscmm | 785 R, 7.2% moisture
XX-D-005 | 1990s DOE Air Toxics Studies | DOE 5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 615 | 606 | Ohio Power Company | bituminous | Eastern | Ohio and Pennsylvania, Pittsburgh #8 seam | Cell | Cardinal Station, Unit 1. ESP eff. = 99 - 99.5%. ESP A SCA = 350-370 ft2/1000 acfm. Stack test conducted during soot blowing and non-sootblowing operations. | 2 |  | 1390 | 1.513 | mg/Nm3 | Good | 1993-06-24 | EPA Method 26, ion chromatography | EPA method 26 | 37633 | dscmm | 788 R, 8.0% moisture
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 1 |  | 83.9 | 0.1119 | mg/Nm3 | Good | 1993-06-23 | SW-846 method 9056 | EPA methods 5/26A | 149900 | dscfm | 27.78 in Hg, 358 deg F, 11.6 % moisture, 14.0/5.3 %CO2/%O2
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 3 |  | 633 | 0.8441 | mg/Nm3 | Good | 1993-06-25 | SW-846 method 9056 | EPA methods 5/26A | 141700 | dscfm | 27.69 in Hg, 331 deg F, 11.3 % moisture, 14.5/4.8 %CO2/%O2
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 5 |  | 1180 | 1.567 | mg/Nm3 | Good | 1993-06-27 | SW-846 method 9056 | EPA methods 5/26A | 142000 | dscfm | 27.72 in Hg, 322 deg F, 11.2 % moisture, 14.5/4.8 %CO2/%O2
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 8 |  | 1220 | 1.695 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 271912 | acfm | 327F, 14.5% CO2, 4.4% O2, 13.98% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 9 |  | 379 | 0.5267 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 273561 | acfm | 339F, 14.6% CO2, 4.3% O2, 13.98% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 7 |  | 1190 | 1.651 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 257317 | acfm | 327F, 14.6% CO2, 4.3% O2, 13.93% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 3 |  | 5.46 | 0.006 | mg/Nm3 | Good | 1997-11-12 | EPA method 26 | EPA method 26 | 713091 | dscfm | 262 F, 11% CO2, 7.7% O2, 81.3% N2, 7.4% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 1 |  | 22.8 | 0.025 | mg/Nm3 | Good | 1997-11-11 | EPA method 26 | EPA method 26 | 708492 | dscfm | 264 F, 11% CO2, 7.7% O2, 81.3% N2, 7.6% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 2 |  | 18.2 | 0.02 | mg/Nm3 | Good | 1997-11-11 | EPA method 26 | EPA method 26 | 701877 | dscfm | 262.25 F, 11% CO2, 7.7% O2, 81.3% N2, 6.8% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 3 |  | 2.76 | 0.003 | mg/Nm3 | Good | 1997-11-14 | EPA method 26 | EPA method 26 | 719552 | dscfm | 185.75 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.7% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 4 |  | 8.27 | 0.009 | mg/Nm3 | Good | 1997-11-14 | EPA method 26 | EPA method 26 | 729618 | dscfm | 185.0 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.8% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 1 |  | 8.27 | 0.009 | mg/Nm3 | Good | 1997-11-13 | EPA method 26 | EPA method 26 | 714245 | dscfm | 187.41 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.7% flue gas moisture
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 5 |  | 7.58 | 0.0076 | mg/Nm3 | Acceptable | 1998-10-17 | unknown | EPA method 26 | 3140168 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 1 |  | 4.59 | 0.0046 | mg/Nm3 | Acceptable | 1998-10-15 | unknown | EPA method 26 | 3081476 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 2 |  | 34 | 0.0341 | mg/Nm3 | Acceptable | 1998-10-16 | unknown | EPA method 26 | 3079853 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 4 |  | 13.2 | 0.0132 | mg/Nm3 | Acceptable | 1998-10-17 | unknown | EPA method 26 | 3100494 | dscfm
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 11 | < | 25.6 | 0.02996 | mg/Nm3 | Good | 2002-06-30 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 8 | < | 25.6 | 0.02996 | mg/Nm3 | Good | 2002-06-28 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 7 |  | 76.8 | 0.08987 | mg/Nm3 | Good | 2002-06-28 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 12 | < | 25.6 | 0.02996 | mg/Nm3 | Good | 2002-06-30 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 5 |  | 51.2 | 0.05992 | mg/Nm3 | Good | 2002-06-27 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 6 | < | 25.6 | 0.02996 | mg/Nm3 | Good | 2002-06-27 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 13 | < | 25.6 | 0.02996 | mg/Nm3 | Good | 2002-07-01 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1, FF | NOx: LNB, PM: FFr | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SD absorber out of service. Reverse air fabric filter only. Variable load 300 - 370 MW during tests. | 10 |  | 282 | 0.3295 | mg/Nm3 | Good | 2002-06-29 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 11 |  | 2130 | 2.994 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 11 |  | 2400 | 3.369 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 9 |  | 2570 | 3.616 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 10 |  | 1820 | 2.554 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 9 |  | 2800 | 3.938 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 10 |  | 1730 | 2.436 | mg/Nm3 | Good | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 4 | < | 768 | 0.8984 | mg/Nm3 | Good | 2008-08-13 | Ion chromatography (IC) | Method 26A | 161013000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 3 |  | 1210 | 1.417 | mg/Nm3 | Good | 2008-08-13 | Ion chromatography (IC) | Method 26A | 161013000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 1 |  | 739 | 0.8639 | mg/Nm3 | Good | 2008-08-12 | Ion chromatography (IC) | Method 26A | 165743000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 25 | < | 25.3 | 0.02954 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 26 | < | 25.3 | 0.02954 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 27 | < | 25.3 | 0.02954 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 1 |  | 419 | 0.49 | mg/Nm3 | Good | 2006-02-16 | Ion chromatography (IC) | EPA Method 26A
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 2 |  | 547 | 0.64 | mg/Nm3 | Good | 2006-02-16 | Ion chromatography (IC) | EPA Method 26A
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 9 |  | 710 | 0.83 | mg/Nm3 | Good | 2006-02-17 | Ion chromatography (IC) | EPA Method 26A
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 | < | 349 | 0.4367 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 396987.7487 | ng/dscm | 0.00034931 | [ | M26A-1 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 | < | 365 | 0.456 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 414549.9359 | ng/dscm | 0.00036476 | [ | M26A-2 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 6440 | 17.57 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26A | 202947 | dscfm | 8.4 % moisture, 10.205475 % CO2, 8.2482563019 % O2, 279.221775 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2105 | ppmv |  |  | 1 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 6150 | 16.65 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26A | 201486 | dscfm | 8.4 % moisture, 10.185575 % CO2, 8.2729263637 % O2, 298.894075 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2060 | ppmv |  |  | 2 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 11800 | 33.03 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | EPA method 26A | 203278 | dscfm | 8.4 % moisture, 10.2312 % CO2, 8.2163649782 % O2, 287.949375 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | ADL | 2054 | ppmv |  |  | 3 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 200 | 0.4596 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1803934 | dscfm | 15.4 % moisture, 10.88 % CO2, 8.62 % O2, 133 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.0645 | ppmv | 0.0002 |  | 1 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 193 | 0.4424 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1824824 | dscfm | 15.3 % moisture, 10.86 % CO2, 8.63 % O2, 132.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. conversion error | ADL | ADL | 0.0549 | ppmv | 0.00017 |  | 2 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 193 | 0.4424 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | EPA method 26A | 1830212 | dscfm | 15.1 % moisture, 10.88 % CO2, 8.64 % O2, 131.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. conversion error | ADL | ADL | 0.0537 | ppmv | 0.00017 |  | 3 | 2056001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 601 | 0.7099 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 645330.2476 | ng/dscm | 0.00060098 |  | M26A-1 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 | < | 290 | 0.3396 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 308718.7705 | ng/dscm | 0.00028962 | [ | M26A-2 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 | < | 300 | 0.3368 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 306169.7717 | ng/dscm | 0.00030048 | [ | M26A-3 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 274 | 0.6821 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1323799 | dscfm | 14.92 % moisture, 11.3 % CO2, 7.2 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.219 | ppmv | 0.000601 |  | 1 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 | < | 143 | 0.3287 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1353712 | dscfm | 14.46 % moisture, 11.4 % CO2, 7.3 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.105] | ppmv | [<0.00029] |  | 2 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 | < | 148 | 0.341 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | EPA method 26A | 1329926 | dscfm | 15.06 % moisture, 10.7 % CO2, 7.9 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.104] | ppmv | [<0.00030] |  | 3 | 1659001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 294 | 0.6759 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2784213 | dscfm | 16.6 % moisture, 11.5 % CO2, 7.5 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.179 | ppmv | 0.000533 |  | 1 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 617 | 1.418 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2704794 | dscfm | 16.7 % moisture, 11.3 % CO2, 7.5 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.21 | ppmv | 0.000617 |  | 2 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 629 | 1.445 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | EPA method 26A | 2738425 | dscfm | 15.6 % moisture, 11.3 % CO2, 7.6 % O2, 123 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 0.218 | ppmv | 0.000629 |  | 3 | 1660001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 501 | 0.5796 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 526884.0262 | ng/dscm | 0.00050054 |  | M26A-1 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 589 | 0.6809 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 619037.516 | ng/dscm | 0.00058896 |  | M26A-2 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 608 | 0.706 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 641831.7281 | ng/dscm | 0.00060838 |  | M26A-3 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 345 | 0.3296 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 299628.8572 | ng/dscm | 0.00034502 | Method M26A DL = Adjusted volume * (mL) * 0.05 ug/mL (lowest calibration standard) See attached detection limit calculation document. | M26A-1 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 800 | 0.7879 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 716274.3536 | ng/dscm | 0.00080023 |  | M26A-2 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 629 | 0.6326 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 575125.0851 | ng/dscm | 0.00062877 |  | M26A-3 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 425 | 0.977 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1442542 | dscfm | 13.2 % moisture, 9.8 % CO2, 9.6 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.102] | ppmv | [<0.000339] |  | 1 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1020 | 2.344 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1421210 | dscfm | 14.7 % moisture, 9.9 % CO2, 9.2 % O2, 128 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.243 | ppmv | 0.000815 |  | 2 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 810 | 1.862 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | EPA method 26A | 1435382 | dscfm | 14.9 % moisture, 9.7 % CO2, 9.1 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.195 | ppmv | 0.000647 |  | 3 | 1666001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 271 | 0.3689 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 335401.3674 | ng/dscm | 0.00027084 | [ | M29-1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 278 | 0.378 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 343654.9829 | ng/dscm | 0.0002775 | [ | M29-2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 278 | 0.3791 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 344607.7794 | ng/dscm | 0.00027827 | [ | M29-3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 271 | 0.5438 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | EPA method 26A | 33509979 | dscfm | 10.9 % moisture, 12.922825 % CO2, 4.4300675899 % O2, 166.89105 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 678 | ppmv |  |  | 1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 278 | 0.5583 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26A | 33768324 | dscfm | 10.9 % moisture, 12.940675 % CO2, 4.4073062648 % O2, 166.671625 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 1931 | ppmv |  |  | 2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 278 | 0.5583 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26A | 33693766 | dscfm | 10.9 % moisture, 12.902275 % CO2, 4.4562209265 % O2, 167.349325 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 1390 | ppmv |  |  | 3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 293 | 0.3996 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 363284.1629 | ng/dscm | 0.00029335 |  | M29-1 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 284 | 0.3839 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 349026.228 | ng/dscm | 0.00028363 |  | M29-2 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 296 | 0.4011 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 364609.2305 | ng/dscm | 0.0002963 | [ | M29-3 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 293 | 0.5868 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 541963 | dscfm | 11.1 % moisture, 12.91349858 % CO2, 4.4049060321 % O2, 245.3452786 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 411 | ppmv |  |  | 1 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 | < | 284 | 0.5684 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 541225 | dscfm | 11.1 % moisture, 12.8878421 % CO2, 4.4376784094 % O2, 244.6899624 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 329 | ppmv |  |  | 2 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 296 | 0.593 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26A | 540995 | dscfm | 11.1 % moisture, 12.88162946 % CO2, 4.4456141427 % O2, 244.9691296 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Emission missing; conversion error. Missing data flag. |  | BDL | 423 | ppmv |  |  | 3 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2145159 | dscfm | 13.3 % moisture, 11.66 % CO2, 7.83 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0594] | ppmv | [<0.00017] | RL based on MDL | 1 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2147440 | dscfm | 13.3 % moisture, 11.67 % CO2, 7.84 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0619] | ppmv | [<0.00018] | RL based on MDL | 2 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2112096 | dscfm | 13.7 % moisture, 11.64 % CO2, 7.88 % O2, 125 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0604] | ppmv | [<0.00018] | RL based on MDL | 3 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 201 | 0.4609 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2145159 | dscfm | 13.3 % moisture, 11.66 % CO2, 7.83 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0594] | ppmv | [<0.00017] | RL based on MDL | 1 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2147440 | dscfm | 13.3 % moisture, 11.67 % CO2, 7.84 % O2, 124.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0619] | ppmv | [<0.00018] | RL based on MDL | 2 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | EPA method 26A | 2112096 | dscfm | 13.7 % moisture, 11.64 % CO2, 7.88 % O2, 125 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0604] | ppmv | [<0.00018] | RL based on MDL | 3 | 2123001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1926479 | dscfm | 12.5 % moisture, 11.39 % CO2, 8.08 % O2, 122.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0575] | ppmv | [<0.00017] | RL based on MDL | 1 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1923024 | dscfm | 12.9 % moisture, 11.45 % CO2, 8.01 % O2, 123.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0570] | ppmv | [<0.00017] | RL based on MDL | 2 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 160 | 0.3677 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | EPA method 26A | 1899892 | dscfm | 12.9 % moisture, 11.42 % CO2, 8 % O2, 124 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0561] | ppmv | [<0.00016] | RL based on MDL | 3 | 2125001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1892416 | dscfm | 12.9 % moisture, 11.58 % CO2, 8.03 % O2, 123.3 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0596] | ppmv | [<0.00017] | RL based on MDL | 1 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 185 | 0.424 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1940845 | dscfm | 12.9 % moisture, 11.64 % CO2, 7.99 % O2, 123.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0584] | ppmv | [<0.00017] | RL based on MDL | 2 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 195 | 0.4486 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | EPA method 26A | 1939495 | dscfm | 13.3 % moisture, 11.64 % CO2, 7.94 % O2, 124.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.0611] | ppmv | [<0.00018] | RL based on MDL | 3 | 2127001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 291 | 0.3741 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 340114.1096 | ng/dscm | 0.00029123 | [ | M26A-1 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 295 | 0.3893 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 353895.9955 | ng/dscm | 0.00029511 | [ | M26A-2 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 298 | 0.3899 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 354493.9027 | ng/dscm | 0.00029755 | [ | M26A-3 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 311 | 0.3992 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 362907.7832 | ng/dscm | 0.00031075 | [ | M26A-1 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 316 | 0.4084 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 371242.3797 | ng/dscm | 0.00031577 | [ | M26A-2 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 316 | 0.4092 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 372034.233 | ng/dscm | 0.00031644 | [ | M26A-3 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 354 | 0.4207 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 382489.1031 | ng/dscm | 0.00035362 | [ | M26A-1 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 347 | 0.4362 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 396590.2817 | ng/dscm | 0.00034657 | [ | M26A-2 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 342 | 0.4304 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 391274.2446 | ng/dscm | 0.00034192 | [ | M26A-3 | 1467