## raw
EPRI Power Plant Toxics Measurement Database
2017-04-18 09:42
Copyright 2015 Electric Power Research Institute (EPRI), Inc. All rights reserved.
Electric Power Research Institute and EPRI are registered service marks of the Electric Power Research Institute, Inc. EPRI.
Stack Emissions Data
Data Sources: All
Selected chemical substances: Hydrogen chloride
Coal Type: All
Selected Chemical: Hydrogen chloride
USGS Province: All
Boiler Type: All
Gas-Side Controls: All Controls
Data Quality: Include All
Non-Detect Data: Use detection limit
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments | Changes to Reported ICR Data | ICR Reported Data Flag | ICR Standardized Data Flag | ICR Reported Concentration | ICR Reported Units of Measure | ICR Emission Factor (lb/million Btu) | ICR Reported Data Comments | ICR Reported Run Number | ICR Submittal ID
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW baseline | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | Baseline tests stored under this unit name. BCCW injection tests stored under Unit 1, BCCW injection. Ash and sulfur reported on dry basis. | 1 |  | 5140 | 6.01 | mg/Nm3 | Acceptable | 1987-11-03 | Ion chromatography (IC), EPA method 300.1 | Not specified | 450000 | dscfm | 8.3% moisture, 267F | dry basis
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW baseline | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | Baseline tests stored under this unit name. BCCW injection tests stored under Unit 1, BCCW injection. Ash and sulfur reported on dry basis. | 2 |  | 7580 | 8.86 | mg/Nm3 | Acceptable | 1987-11-04 | Ion chromatography (IC), EPA method 300.1 | Not specified | 447000 | dscfm | 7.8% moisture, 264F | dry basis. Reported as ppmv and converted to mg/Nm3.
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW baseline | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | Baseline tests stored under this unit name. BCCW injection tests stored under Unit 1, BCCW injection. Ash and sulfur reported on dry basis. | 4 |  | 10000 | 11.7 | mg/Nm3 | Acceptable | 1987-11-05 | Ion chromatography (IC), EPA method 300.1 | Not specified | 408000 | dscfm | 7.3% moisture, 257F | dry basis. Reported as ppmv and converted to mg/Nm3.
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW baseline | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | Baseline tests stored under this unit name. BCCW injection tests stored under Unit 1, BCCW injection. Ash and sulfur reported on dry basis. | 5 |  | 9490 | 11.1 | mg/Nm3 | Acceptable | 1987-11-06 | Ion chromatography (IC), EPA method 300.1 | Not specified | 412000 | dscfm | 7.1% moisture, 235F | dry basis. Reported as ppmv and converted to mg/Nm3.
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW injection | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | BCCW injection tests stored under this unit name. Baseline injection tests stored under Unit 1, BCCW baseline. Ash and sulfur reported on dry basis. | 1 |  | 5550 | 6.49 | mg/Nm3 | Acceptable | 1987-11-08 | Ion chromatography (IC), EPA method 300.1 | Not specified | 412000 | dscfm | 9.6% moisture, 288F | Dry basis, BCCW-EDTA evaporation. Reported as ppmv and converted to mg/Nm3.
BE-X-001 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Unit 1, BCCW injection | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 200 |  | Southeastern US | bituminous | Unknown |  | Front-fired | BCCW injection tests stored under this unit name. Baseline injection tests stored under Unit 1, BCCW baseline. Ash and sulfur reported on dry basis. | 3 |  | 6760 | 7.91 | mg/Nm3 | Acceptable | 1987-11-08 | Ion chromatography (IC), EPA method 300.1 | Not specified | 412000 | dscfm | 10.1% moisture, 288F | Dry basis, BCCW-EDTA evaporation. Reported as ppmv and converted to mg/Nm3.
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 1 |  | 555 | 0.639 | mg/Nm3 | Acceptable | 1981-03-17 | Not specified | Not specified | 332 | m3/sec
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 3 |  | 95.5 | 0.11 | mg/Nm3 | Acceptable | 1981-03-17 | Not specified | Not specified | 335 | m3/sec
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 4 |  | 858 | 0.989 | mg/Nm3 | Acceptable | 1981-03-18 | Not specified | Not specified | 289 | m3/sec
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 6 |  | 1510 | 1.741 | mg/Nm3 | Acceptable | 1981-03-18 | Not specified | Not specified | 342 | m3/sec |  | 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 7 |  | 2360 | 2.723 | mg/Nm3 | Acceptable | 1981-03-18 | Not specified | Not specified | 362 | m3/sec
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 8 |  | 1830 | 2.108 | mg/Nm3 | Acceptable | 1981-03-19 | Not specified | Not specified | 293 | m3/sec |  | 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 10 |  | 1580 | 1.822 | mg/Nm3 | Acceptable | 1981-03-19 | Not specified | Not specified | 348 | m3/sec |  | 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Battle River - B | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Alberta Power, Ltd. | subbituminous | Unknown | Battle River Mine, subbituminous C, Alberta | Tangential | B-plant consists of Units 3 & 4 - common stack | 11 |  | 1900 | 2.193 | mg/Nm3 | Acceptable | 1981-03-19 | Not specified | Not specified | 347 | m3/sec
EV-00086 | General Historical Literature Studies | Lingan | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 320 |  | Nova Scotia Power Corp. | bituminous | Unknown | Nova Scotia local, Cape Breton | Tangential | Two units - common stack. Two test blocks: (1) economizer inlet and (2) stack gas. | 5 |  | 54700 | 70.17 | mg/Nm3 | Acceptable | 1981-12-08 | Not specified | Not specified | 236 | m3/sec |  | Vapor phase trace elements. 50% mass balance closure
EV-00086 | General Historical Literature Studies | Lingan | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 320 |  | Nova Scotia Power Corp. | bituminous | Unknown | Nova Scotia local, Cape Breton | Tangential | Two units - common stack. Two test blocks: (1) economizer inlet and (2) stack gas. | 4 |  | 71600 | 91.85 | mg/Nm3 | Acceptable | 1981-12-08 | Not specified | Not specified | 235 | m3/sec |  | Vapor phase trace elements. 50% mass balance closure
EV-00086 | General Historical Literature Studies | Lingan | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 320 |  | Nova Scotia Power Corp. | bituminous | Unknown | Nova Scotia local, Cape Breton | Tangential | Two units - common stack. Two test blocks: (1) economizer inlet and (2) stack gas. | 3 |  | 77800 | 99.7 | mg/Nm3 | Acceptable | 1981-12-07 | Not specified | Not specified | 248 | m3/sec |  | Vapor phase trace elements. 50% mass balance closure
EV-00086 | General Historical Literature Studies | Lingan | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 320 |  | Nova Scotia Power Corp. | bituminous | Unknown | Nova Scotia local, Cape Breton | Tangential | Two units - common stack. Two test blocks: (1) economizer inlet and (2) stack gas. | 7 |  | 57200 | 73.38 | mg/Nm3 | Acceptable | 1981-12-09 | Not specified | Not specified |  |  |  | Vapor phase trace elements
EV-00086 | General Historical Literature Studies | Lingan | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 320 |  | Nova Scotia Power Corp. | bituminous | Unknown | Nova Scotia local, Cape Breton | Tangential | Two units - common stack. Two test blocks: (1) economizer inlet and (2) stack gas. | 6 |  | 65000 | 83.31 | mg/Nm3 | Acceptable | 1981-12-09 | Not specified | Not specified | 260 | m3/sec |  | Vapor phase trace elements. 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Nanticoke Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 500 |  |  | bituminous | Unknown | Washed USA and Canada bituminous coal; Alberta and West Virginia | Wall-fired | Eight 500 MW plants at station | 2 |  | 274000 | 304.2 | mg/Nm3 | Poor | 1982-07-08 | Not specified | Not specified | 808 | m3/sec |  | 200-300% mass balance closure.
EV-00086 | General Historical Literature Studies | Nanticoke Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 500 |  |  | bituminous | Unknown | Washed USA and Canada bituminous coal; Alberta and West Virginia | Wall-fired | Eight 500 MW plants at station | 1 |  | 207000 | 229.8 | mg/Nm3 | Poor | 1982-07-07 | Not specified | Not specified | 800 | m3/sec |  | 200-300% mass balance closure.
EV-00086 | General Historical Literature Studies | Nanticoke Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 500 |  |  | bituminous | Unknown | Washed USA and Canada bituminous coal; Alberta and West Virginia | Wall-fired | Eight 500 MW plants at station | 3 |  | 216000 | 239.7 | mg/Nm3 | Poor | 1982-07-09 | Not specified | Not specified | 836 | m3/sec |  | 200-300% mass balance closure.
EV-00086 | General Historical Literature Studies | Nanticoke Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 500 |  |  | bituminous | Unknown | Washed USA and Canada bituminous coal; Alberta and West Virginia | Wall-fired | Eight 500 MW plants at station | 5 |  | 234000 | 259.9 | mg/Nm3 | Poor | 1982-07-10 | Not specified | Not specified | 512 | m3/sec |  | 200-300% mass balance closure.
EV-00086 | General Historical Literature Studies | Poplar River Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Saskatchewan Power Corp. | lignite | Unknown | Local, Saskatchewan | Wall-fired | Two units at station | 4 |  | 3020 | 2.587 | mg/Nm3 | Acceptable | 1982-06-19 | Not specified | Not specified | 606 | m3/sec |  | Vapor phase elements. 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Poplar River Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Saskatchewan Power Corp. | lignite | Unknown | Local, Saskatchewan | Wall-fired | Two units at station | 3 |  | 3060 | 2.624 | mg/Nm3 | Acceptable | 1982-06-18 | Not specified | Not specified | 597 | m3/sec |  | Vapor phase elements. 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Poplar River Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Saskatchewan Power Corp. | lignite | Unknown | Local, Saskatchewan | Wall-fired | Two units at station | 1 |  | 3680 | 3.149 | mg/Nm3 | Acceptable | 1982-06-16 | Not specified | Not specified | 630 | m3/sec |  | Vapor phase elements. 50% mass balance closure.
EV-00086 | General Historical Literature Studies | Poplar River Unit 2 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Saskatchewan Power Corp. | lignite | Unknown | Local, Saskatchewan | Wall-fired | Two units at station | 2 |  | 3220 | 2.756 | mg/Nm3 | Acceptable | 1982-06-17 | Not specified | Not specified | 625 | m3/sec |  | Vapor phase elements. 50% mass balance closure.
GL-00074 | General Historical Literature Studies | Chalk Point Unit 1 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 355 |  | Potomac Electric Power Co. | bituminous | Eastern | Pennsylvania and West Virginia | Wall-fired | Solid waste disposal methods not specified, data also presented for GE-S-00367 in database. | 12 | > | 12800 | 15 | mg/Nm3 | Acceptable | 1979-07-24 | Instrumental neutron activation analysis (INAA) | EPA modified method |  |  |  | Value reported is average of 10-12 measurements, total variability is +/- reported units; Concentration given as lower limit.
LI-R-00483 | General Historical Literature Studies | RD Morrow Unit 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 200 |  | Southern Mississippi Electric Power Assoc. | bituminous | Unknown |  | Wall-fired | Rod deck type absorber, coal has 0.1% chloride. | 2 |  | 7840 | 9.174 | mg/Nm3 | Unknown * | 1983-08-11 | Not specified | Not specified |  |  |  | reported as ppmv of the acid gas
LI-R-00483 | General Historical Literature Studies | RD Morrow Unit 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 200 |  | Southern Mississippi Electric Power Assoc. | bituminous | Unknown |  | Wall-fired | Rod deck type absorber, coal has 0.1% chloride. | 1 |  | 7980 | 9.332 | mg/Nm3 | Unknown * | 1983-08-11 | Not specified | Not specified |  |  |  | reported as ppmv of the acid gas
LI-R-00483 | General Historical Literature Studies | RD Morrow Unit 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 200 |  | Southern Mississippi Electric Power Assoc. | bituminous | Unknown |  | Wall-fired | Rod deck type absorber, coal has 0.1% chloride. | 3 |  | 5000 | 5.852 | mg/Nm3 | Unknown * | 1983-09-15 | Not specified | Not specified |  |  |  | reported as ppmv of the acid gas
LI-R-00483 | General Historical Literature Studies | RD Morrow Unit 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 200 |  | Southern Mississippi Electric Power Assoc. | bituminous | Unknown |  | Wall-fired | Rod deck type absorber, coal has 0.1% chloride. | 4 |  | 13500 | 15.82 | mg/Nm3 | Unknown * | 1983-09-16 | Not specified | Not specified |  |  |  | reported as ppmv of the acid gas
ME-S-00587 | General Historical Literature Studies | Amer Power Station - Unit AC4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers |  | 207 | Netherlands | bituminous | Eastern | Eastern USA | Tangential | Moisture free coal used | 1 |  | 60300 | 77 | mg/Nm3 | Acceptable | 1984-09-12 | Not specified | Not specified | 180 | m3/sec | 130 C
ME-S-00587 | General Historical Literature Studies | Amer Power Station - Unit AC5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers |  | 200 | Netherlands | bituminous | Eastern | Eastern USA | Tangential | Moisture free coal used | 1 |  | 49700 | 55 | mg/Nm3 | Acceptable | 1983-03-21 | Not specified | Not specified | 20 | kg/hr | 130 C
ME-S-00587 | General Historical Literature Studies | Amer Power Station - Unit AC8 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers |  | 596 | Netherlands | bituminous | Eastern | Eastern USA | Tangential | Moisture free coal used. Coal characteristics, consumption and gen. output are average of two test runs | 1 |  | 45800 | 55 | mg/Nm3 | Acceptable | 1983-03-21 | Not specified | Not specified | 500 | m3/sec | 125 C | Concentration is the average of a given range; calculated from coal consumption
ME-S-00587 | General Historical Literature Studies | Amer Power Station - Unit AC8 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers |  | 596 | Netherlands | bituminous | Eastern | Eastern USA | Tangential | Moisture free coal used. Coal characteristics, consumption and gen. output are average of two test runs | 2 |  | 63200 | 76 | mg/Nm3 | Acceptable | 1984-09-12 | Not specified | Not specified | 500 | m3/sec | 116 C
MI-X-001 | General Historical Literature Studies | Cordemais 4 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 600 | 580 |  | Unknown | Unknown | Australia | Unknown | see also MI-X-002, MI-X-003 | 1 |  | 17200 | 24 | mg/Nm3 | Unknown * | 1984-10-24 | Selective ion electrode (SIE) | Isokinetic probe | 1850000 | Nm3/hr
MI-X-001 | General Historical Literature Studies | Le Havre 4 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 600 |  |  | Unknown | Unknown | South Africa or Australia | Unknown | see also MI-X-002, MI-X-003 | 7 |  | 15500 | 21 | mg/Nm3 | Unknown * | 1986-02-25 | Selective ion electrode (SIE) | Isokinetic probe | 1910000 | Nm3/hr
MI-X-001 | General Historical Literature Studies | Le Havre 4 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 600 |  |  | Unknown | Unknown | South Africa or Australia | Unknown | see also MI-X-002, MI-X-003 | 5 |  | 40000 | 54 | mg/Nm3 | Unknown * | 1985-03-13 | Selective ion electrode (SIE) | Isokinetic probe | 2088000 | Nm3/hr
MI-X-001 | General Historical Literature Studies | Le Havre 4 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 600 |  |  | Unknown | Unknown | South Africa or Australia | Unknown | see also MI-X-002, MI-X-003 | 4 |  | 15500 | 21 | mg/Nm3 | Unknown * | 1985-03-12 | Selective ion electrode (SIE) | Isokinetic probe | 657400 | Nm3/hr
MI-X-001 | General Historical Literature Studies | Porcheville A 3 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 125 | 93 |  | Unknown | Unknown | Australia and Columbia, 1:1 mix | Unknown | see also MI-X-002 | 1 |  | 52400 | 55 | mg/Nm3 | Unknown * | 1984-10-30 | Selective ion electrode (SIE) | Isokinetic probe | 392000 | Nm3/hr
MI-X-002 | General Historical Literature Studies | Vitry 2 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 250 | 220 |  | Unknown | Unknown | Poland | Unknown | See also MI-X-001 and MI-X-003. | 4 |  | 98600 | 145 | mg/Nm3 | Unknown * | 1984-03-24 | Selective ion electrode (SIE) | Isokinetic probe | 661440 | Nm3/hr
SM-00285 | General Historical Literature Studies | Conesville Unit 5 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Turbulent Contact Absorber) | Coal-Fired Boilers | 411 |  | Columbus and Southern Ohio Electric Co. | bituminous | Eastern | Ohio | Tangential | Two TCA FGD modules | 1 |  | 2230 | 2.87 | mg/Nm3 | Acceptable | 1978-11-09 | Not specified | Controlled condensation train |  |  |  | Vapor phase chloride expressed as HCl.
SM-00285 | General Historical Literature Studies | Conesville Unit 5 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Turbulent Contact Absorber) | Coal-Fired Boilers | 411 |  | Columbus and Southern Ohio Electric Co. | bituminous | Eastern | Ohio | Tangential | Two TCA FGD modules | 3 |  | 1960 | 2.52 | mg/Nm3 | Acceptable | 1978-11-14 | Not specified | Controlled condensation train |  |  |  | Vapor phase chloride expressed as HCl.
SM-00285 | General Historical Literature Studies | Conesville Unit 5 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Turbulent Contact Absorber) | Coal-Fired Boilers | 411 |  | Columbus and Southern Ohio Electric Co. | bituminous | Eastern | Ohio | Tangential | Two TCA FGD modules | 6 |  | 1090 | 1.4 | mg/Nm3 | Acceptable | 1978-11-16 | Not specified | Controlled condensation train |  |  |  | Vapor phase chloride expressed as HCl.
SM-00285 | General Historical Literature Studies | Conesville Unit 5 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Turbulent Contact Absorber) | Coal-Fired Boilers | 411 |  | Columbus and Southern Ohio Electric Co. | bituminous | Eastern | Ohio | Tangential | Two TCA FGD modules | 8 |  | 179 | 0.23 | mg/Nm3 | Acceptable | 1979-10-05 | Not specified | Controlled condensation train |  |  |  | Vapor phase chloride expressed as HCl.
SM-00285 | General Historical Literature Studies | Conesville Unit 5 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Turbulent Contact Absorber) | Coal-Fired Boilers | 411 |  | Columbus and Southern Ohio Electric Co. | bituminous | Eastern | Ohio | Tangential | Two TCA FGD modules | 10 |  | 179 | 0.23 | mg/Nm3 | Acceptable | 1979-10-07 | Not specified | Controlled condensation train |  |  |  | Vapor phase chloride expressed as HCl.
TH-X-002 | General Historical Literature Studies | LTGS Unit 3 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 1 |  | 51500 | 60.25 | mg/Nm3 | Acceptable | 1989-10-23 | Ion chromatography (IC) | EPA modified method 5 | 50 | dscm/s | Temp=118 C, H2O=4.80% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 3 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 2 |  | 46800 | 54.73 | mg/Nm3 | Acceptable | 1989-10-24 | Ion chromatography (IC) | EPA modified method 5 | 47 | dscm/s | Temp=117 C, H2O=4.98% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 1 |  | 89600 | 104.8 | mg/Nm3 | Acceptable | 1989-12-01 | Ion chromatography (IC) | EPA modified method 5 | 53 | dscm/s | Temp=127 C, H2O=6.17% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 2 |  | 103000 | 120 | mg/Nm3 | Acceptable | 1989-12-05 | Ion chromatography (IC) | EPA modified method 5 | 80 | dscm/s | Temp=138 C, H2O=6.63% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 3 |  | 87500 | 102.3 | mg/Nm3 | Acceptable | 1989-12-06 | Ion chromatography (IC) | EPA modified method 5 | 66 | dscm/s | Temp=132 C, H2O=5.41% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 4 |  | 88300 | 103.3 | mg/Nm3 | Acceptable | 1989-12-07 | Ion chromatography (IC) | EPA modified method 5 | 58 | dscm/s | Temp=142 C, H2O=6.48% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 5 |  | 65500 | 76.57 | mg/Nm3 | Acceptable | 1989-12-10 | Ion chromatography (IC) | EPA modified method 5 | 49 | dscm/s | Temp=129 C, H2O=5.30% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 6 |  | 144000 | 168.5 | mg/Nm3 | Acceptable | 1989-12-11 | Ion chromatography (IC) | EPA modified method 5 | 80 | dscm/s | Temp=136 C, H2O=6.73% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 4 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Tangential |  | 7 |  | 146000 | 171.3 | mg/Nm3 | Acceptable | 1989-12-12 | Ion chromatography (IC) | EPA modified method 5 | 79 | dscm/s | Temp=130 C, H2O=6.71% | Concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 9 |  | 49700 | 58.09 | mg/Nm3 | Acceptable | 1989-10-12 | Ion chromatography (IC) | EPA modified method 5 | 40 | dscm/s | Temp=106 C, H2O=4.23% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 3 |  | 108000 | 126.8 | mg/Nm3 | Acceptable | 1989-10-05 | Ion chromatography (IC) | EPA modified method 5 | 74 | dscm/s | Temp=129 C, H2O=6.61% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 8 |  | 51700 | 60.43 | mg/Nm3 | Acceptable | 1989-10-11 | Ion chromatography (IC) | EPA modified method 5 | 42 | dscm/s | Temp=108 C, H2O=4.47% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 2 |  | 91000 | 106.4 | mg/Nm3 | Acceptable | 1989-10-04 | Ion chromatography (IC) | EPA modified method 5 | 75 | dscm/s | Temp=130 C, H2O=6.24% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 7 |  | 56600 | 66.24 | mg/Nm3 | Acceptable | 1989-10-10 | Ion chromatography (IC) | EPA modified method 5 | 43 | dscm/s | Temp=106 C, H2O=4.68% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 1 |  | 89300 | 104.5 | mg/Nm3 | Acceptable | 1989-10-03 | Ion chromatography (IC) | EPA modified method 5 | 73 | dscm/s | Temp=130 C, H2O=6.3% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 6 |  | 80800 | 94.5 | mg/Nm3 | Acceptable | 1989-10-08 | Ion chromatography (IC) | EPA modified method 5 | 55 | dscm/s | Temp=115 C, H2O=5.98% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 5 |  | 90400 | 105.7 | mg/Nm3 | Acceptable | 1989-10-07 | Ion chromatography (IC) | EPA modified method 5 | 55 | dscm/s | Temp=116 C, H2O=5.94% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
TH-X-002 | General Historical Literature Studies | LTGS Unit 7 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 300 |  | Ontario Hydro | bituminous | Eastern | Eastern | Wall-fired |  | 4 |  | 79600 | 93.08 | mg/Nm3 | Acceptable | 1989-10-06 | Ion chromatography (IC) | EPA modified method 5 | 54 | dscm/s | Temp=119 C, H2O=6.18% | Concentrations in impingers were unexpectedly high for several elements; concentrations are on a dry basis at 25 deg. C and 1 atm.
XX-D-001 | 1990s DOE Air Toxics Studies | DOE 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 528 | 528 | Northern Indiana Public Service Company (NIPSCO) | bituminous | Interior(East, North) | Illinois/Indiana | Cyclone | Bailly Station, Units 7 and 8. ESP eff. = 99.9%. AFGD scrubber process. Unit 7 and 8 ESP outlets combine before entering the AFGD scrubber. Load is for Unit 7 and 8 combined. Ammonia injection at ESP inlets controlled at 15 ppm. No injection on 9/5. | 2 |  | 927 | 1.254 | mg/Nm3 | Good | 1993-09-04 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 835 | kg/s | Dry flow rate at 3% oxygen.
XX-D-001 | 1990s DOE Air Toxics Studies | DOE 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 528 | 528 | Northern Indiana Public Service Company (NIPSCO) | bituminous | Interior(East, North) | Illinois/Indiana | Cyclone | Bailly Station, Units 7 and 8. ESP eff. = 99.9%. AFGD scrubber process. Unit 7 and 8 ESP outlets combine before entering the AFGD scrubber. Load is for Unit 7 and 8 combined. Ammonia injection at ESP inlets controlled at 15 ppm. No injection on 9/5. | 3 |  | 1090 | 1.481 | mg/Nm3 | Good | 1993-09-05 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 817 | kg/s | Dry flow rate at 3% oxygen.
XX-D-001 | 1990s DOE Air Toxics Studies | DOE 1 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 528 | 528 | Northern Indiana Public Service Company (NIPSCO) | bituminous | Interior(East, North) | Illinois/Indiana | Cyclone | Bailly Station, Units 7 and 8. ESP eff. = 99.9%. AFGD scrubber process. Unit 7 and 8 ESP outlets combine before entering the AFGD scrubber. Load is for Unit 7 and 8 combined. Ammonia injection at ESP inlets controlled at 15 ppm. No injection on 9/5. | 1 |  | 1120 | 1.521 | mg/Nm3 | Good | 1993-09-03 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 805 | kg/s | Dry flow rate at 3% oxygen.
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2 | NOx: Unspecified, PM: ESPc(Without conditioning) | Coal-Fired Boilers | 115 | 108 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station, Unit 2. ESP eff. = 98.7%. Ammonia injection system for ESPs was turned off during the test program. | 4 |  | 131000 | 217.8 | mg/Nm3 | Good | 1993-07-29 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 5093 | Ncm/min | 293 F, -0.08 in Hg relative to atmospheric, 9.4% moisture, 6.5% oxygen
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2 | NOx: Unspecified, PM: ESPc(Without conditioning) | Coal-Fired Boilers | 115 | 108 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station, Unit 2. ESP eff. = 98.7%. Ammonia injection system for ESPs was turned off during the test program. | 6 |  | 132000 | 218.7 | mg/Nm3 | Good | 1993-07-31 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 5120 | Ncm/min | 291 F, -0.08 in Hg relative to atmospheric, 9.4% moisture, 6.5% oxygen
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2 | NOx: Unspecified, PM: ESPc(Without conditioning) | Coal-Fired Boilers | 115 | 108 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station, Unit 2. ESP eff. = 98.7%. Ammonia injection system for ESPs was turned off during the test program. | 2 |  | 133000 | 221.3 | mg/Nm3 | Good | 1993-07-27 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 5316 | Ncm/min | 294 F, -0.07 in Hg relative to atmospheric, 9.2% moisture, 6.0% oxygen
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2, SNOx | NOx: SNOx, PM: FF, SO2: FGDsnox | Coal-Fired Boilers | 31 | 29 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station demonstration of a pilot-scale SNOx system. Baghouse eff. = 99.3%. SNOx unit treated approximately 27% of the flue gas. Wet gas sulfuric acid (WSA)-SCR process. | 4 |  | 98900 | 136.8 | mg/Nm3 | Good | 1993-07-22 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 1419 | Ncm/min | 365 K, 1.52 mm Hg relative to atmospheric, 8.1% moisture, 6.0% oxygen
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2, SNOx | NOx: SNOx, PM: FF, SO2: FGDsnox | Coal-Fired Boilers | 31 | 29 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station demonstration of a pilot-scale SNOx system. Baghouse eff. = 99.3%. SNOx unit treated approximately 27% of the flue gas. Wet gas sulfuric acid (WSA)-SCR process. | 6 |  | 68500 | 94.78 | mg/Nm3 | Good | 1993-07-24 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 1406 | Ncm/min | 366 K, 1.52 mm Hg relative to atmospheric, 8.0% moisture, 8.0% oxygen
XX-D-002 | 1990s DOE Air Toxics Studies | DOE 2, SNOx | NOx: SNOx, PM: FF, SO2: FGDsnox | Coal-Fired Boilers | 31 | 29 | Ohio Edison | bituminous | Eastern | Ohio/PA, seams 6,7, and Kittanning/Freeport | Cyclone | Niles Station demonstration of a pilot-scale SNOx system. Baghouse eff. = 99.3%. SNOx unit treated approximately 27% of the flue gas. Wet gas sulfuric acid (WSA)-SCR process. | 2 |  | 79000 | 109.2 | mg/Nm3 | Good | 1993-07-19 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 1694 | Ncm/min | 365 K, 1.52 mm Hg relative to atmospheric, 9.0% moisture, 6.0% oxygen
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 5 |  | 76700 | 101.2 | mg/Nm3 | Good | 1993-07-15 | EPA method 9056 | EPA method 5 and 26A | 1242000 | dscfm | 29.45 in Hg, 336 deg F, 10.5 % moisture, 14.2/4.7 %CO2/%O2
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 8 |  | 79900 | 105.4 | mg/Nm3 | Good | 1993-07-19 | EPA method 9056 | EPA method 5 and 26A | 1181200 | dscfm | 29.42 in Hg, 331 deg F, 10.2 % moisture, 14.4/4.7 %CO2/%O2
XX-D-003 | 1990s DOE Air Toxics Studies | DOE 3 | NOx: FGR, PM: ESPc | Coal-Fired Boilers | 568 |  | Illinois Power Company | bituminous | Interior(East, North) | Illinois | Cyclone | Baldwin Station, Unit 2. ESP eff. = 96-97%. Bottom ash and fly ash sluiced to separate ponds. Ash pond outfalls sent to common tertiary pond w/ discharge to river. Coal washing for SO2 compliance. ESP SCA = 180 ft2/1000 acfm. | 2 |  | 81500 | 107.5 | mg/Nm3 | Good | 1993-07-13 | EPA method 9056 | EPA method 5 and 26A | 1199200 | dscfm | 29.39 in Hg, 339 deg F, 10.4 % moisture, 14.2/4.7 %CO2/%O2
XX-D-004 | 1990s DOE Air Toxics Studies | DOE 4 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Jet Bubble Reactor,Forced ox) | Coal-Fired Boilers | 123 | 101 | Georgia Power Company | bituminous | Interior(East, North) | Illinois No. 5 and No. 6 | Tangential | Plant Yates, Unit 1. ESP eff. = 98-99%. ESP SCA = 210 ft2/Kacfm. FGD system is the Chiyoda Thoroughbred (CT)-121 process. | 4 |  | 290 | 0.2943 | mg/Nm3 | Acceptable | 1993-06-25 | EPA method 300.0, ion chromotography | Filter, impinger train - H2O2, NaCO3, NaHCO3 | 272827 | dscfm | 29.26 in Hg, 593 deg R, 14.6% Moisture, 11.3/7.5 %CO2/%O2
XX-D-004 | 1990s DOE Air Toxics Studies | DOE 4 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Jet Bubble Reactor,Forced ox) | Coal-Fired Boilers | 123 | 101 | Georgia Power Company | bituminous | Interior(East, North) | Illinois No. 5 and No. 6 | Tangential | Plant Yates, Unit 1. ESP eff. = 98-99%. ESP SCA = 210 ft2/Kacfm. FGD system is the Chiyoda Thoroughbred (CT)-121 process. | 6 |  | 404 | 0.4106 | mg/Nm3 | Acceptable | 1993-06-27 | EPA method 300.0, ion chromotography | Filter, impinger train - H2O2, NaCO3, NaHCO3 | 280900 | dscfm | 29.26 in Hg, 593 deg R, 14.6% Moisture, 11.3/7.5 %CO2/%O2
XX-D-004 | 1990s DOE Air Toxics Studies | DOE 4 | NOx: Unspecified, PM: ESPc, SO2: FGDw(Jet Bubble Reactor,Forced ox) | Coal-Fired Boilers | 123 | 101 | Georgia Power Company | bituminous | Interior(East, North) | Illinois No. 5 and No. 6 | Tangential | Plant Yates, Unit 1. ESP eff. = 98-99%. ESP SCA = 210 ft2/Kacfm. FGD system is the Chiyoda Thoroughbred (CT)-121 process. | 5 |  | 900 | 0.9142 | mg/Nm3 | Acceptable | 1993-06-26 | EPA method 300.0, ion chromotography | Filter, impinger train - H2O2, NaCO3, NaHCO3 | 276537 | dscfm | 29.26 in Hg, 593 deg R, 14.6% Moisture, 11.3/7.5 %CO2/%O2
XX-D-005 | 1990s DOE Air Toxics Studies | DOE 5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 615 | 606 | Ohio Power Company | bituminous | Eastern | Ohio and Pennsylvania, Pittsburgh #8 seam | Cell | Cardinal Station, Unit 1. ESP eff. = 99 - 99.5%. ESP A SCA = 350-370 ft2/1000 acfm. Stack test conducted during soot blowing and non-sootblowing operations. | 1 |  | 25100 | 27.36 | mg/Nm3 | Poor | 1993-06-23 | EPA Method 26, ion chromatography | EPA method 26 | 36596 | dscmm | 785 R, 7.1% moisture | This compound was detected, but the lack of QA data precludes a reliable quantification of the levels.
XX-D-005 | 1990s DOE Air Toxics Studies | DOE 5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 615 | 606 | Ohio Power Company | bituminous | Eastern | Ohio and Pennsylvania, Pittsburgh #8 seam | Cell | Cardinal Station, Unit 1. ESP eff. = 99 - 99.5%. ESP A SCA = 350-370 ft2/1000 acfm. Stack test conducted during soot blowing and non-sootblowing operations. | 3 |  | 27100 | 29.51 | mg/Nm3 | Poor | 1993-06-25 | EPA Method 26, ion chromatography | EPA method 26 | 37247 | dscmm | 785 R, 7.2% moisture | This compound was detected, but the lack of QA data precludes a reliable quantification of the levels.
XX-D-005 | 1990s DOE Air Toxics Studies | DOE 5 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 615 | 606 | Ohio Power Company | bituminous | Eastern | Ohio and Pennsylvania, Pittsburgh #8 seam | Cell | Cardinal Station, Unit 1. ESP eff. = 99 - 99.5%. ESP A SCA = 350-370 ft2/1000 acfm. Stack test conducted during soot blowing and non-sootblowing operations. | 2 |  | 21500 | 23.39 | mg/Nm3 | Poor | 1993-06-24 | EPA Method 26, ion chromatography | EPA method 26 | 37633 | dscmm | 788 R, 8.0% moisture | This compound was detected, but the lack of QA data precludes a reliable quantification of the levels.
XX-D-006 | 1990s DOE Air Toxics Studies | DOE 6 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 570 | 564 | Cooperative Power Association | lignite | Northern Great Plains | North Dakota, Falkirk Mine | Tangential | Coal Creek Station, Unit 1. ESP eff. = 99.5%. 59% FGD flue gas bypass. ESP SCA = 599 ft2/1000 acfm. Zero discharge mine-mouth plant. | 2 |  | 1480 | 1.98 | mg/Nm3 | Good | 1993-06-22 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 30688 | Nm3/min | 121 C, -0.1 in. Hg relative to atmospheric, 17.0% moisture, 8% oxygen
XX-D-006 | 1990s DOE Air Toxics Studies | DOE 6 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 570 | 564 | Cooperative Power Association | lignite | Northern Great Plains | North Dakota, Falkirk Mine | Tangential | Coal Creek Station, Unit 1. ESP eff. = 99.5%. 59% FGD flue gas bypass. ESP SCA = 599 ft2/1000 acfm. Zero discharge mine-mouth plant. | 4 |  | 1280 | 1.72 | mg/Nm3 | Good | 1993-06-24 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 30677 | Nm3/min | 111 C, -0.2 in. Hg relative to atmospheric, 16.9% moisture, 8% oxygen
XX-D-006 | 1990s DOE Air Toxics Studies | DOE 6 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 570 | 564 | Cooperative Power Association | lignite | Northern Great Plains | North Dakota, Falkirk Mine | Tangential | Coal Creek Station, Unit 1. ESP eff. = 99.5%. 59% FGD flue gas bypass. ESP SCA = 599 ft2/1000 acfm. Zero discharge mine-mouth plant. | 6 |  | 1260 | 1.69 | mg/Nm3 | Good | 1993-06-27 | Ion chromatography (IC), EPA method 300.1 | EPA method 26A | 30166 | Nm3/min | 107 C, -0.1 in. Hg relative to atmospheric, 17.1% moisture, 8% oxygen
XX-D-007 | 1990s DOE Air Toxics Studies | DOE 7 | NOx: OFA, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 422 | 420 | Tucson Electric Power Company | subbituminous | Rocky Mountain | New Mexico, Lee Ranch Mine | Corner-fired | Springerville Generating Station, Unit 2. FF eff. = 99.9%. Joy/Niro SD/FF system. Lime source Chemstar Lime, Nelson, AZ. Zero discharge station. 10% flue gas bypass around SD/FF system during test. | 4 |  | 133 | 0.189 | mg/Nm3 | Acceptable | 1993-06-05 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 389 | Nm3/sec | Dry flow rate at 3% oxygen.
XX-D-007 | 1990s DOE Air Toxics Studies | DOE 7 | NOx: OFA, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 422 | 420 | Tucson Electric Power Company | subbituminous | Rocky Mountain | New Mexico, Lee Ranch Mine | Corner-fired | Springerville Generating Station, Unit 2. FF eff. = 99.9%. Joy/Niro SD/FF system. Lime source Chemstar Lime, Nelson, AZ. Zero discharge station. 10% flue gas bypass around SD/FF system during test. | 5 |  | 90.8 | 0.129 | mg/Nm3 | Acceptable | 1993-06-08 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 352 | Nm3/sec | Dry flow rate at 3% oxygen.
XX-D-007 | 1990s DOE Air Toxics Studies | DOE 7 | NOx: OFA, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 422 | 420 | Tucson Electric Power Company | subbituminous | Rocky Mountain | New Mexico, Lee Ranch Mine | Corner-fired | Springerville Generating Station, Unit 2. FF eff. = 99.9%. Joy/Niro SD/FF system. Lime source Chemstar Lime, Nelson, AZ. Zero discharge station. 10% flue gas bypass around SD/FF system during test. | 2 |  | 137 | 0.195 | mg/Nm3 | Acceptable | 1993-06-03 | Ion chromatography (IC) | MM5 with carbonate/bicarbonate/peroxide solution | 341 | Nm3/sec | Dry flow rate at 3% oxygen.
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 1 |  | 560 | 0.747 | mg/Nm3 | Good | 1993-06-23 | SW-846 method 9056 | EPA methods 5/26A | 149900 | dscfm | 27.78 in Hg, 358 deg F, 11.6 % moisture, 14.0/5.3 %CO2/%O2
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 3 |  | 836 | 1.114 | mg/Nm3 | Good | 1993-06-25 | SW-846 method 9056 | EPA methods 5/26A | 141700 | dscfm | 27.69 in Hg, 331 deg F, 11.3 % moisture, 14.5/4.8 %CO2/%O2
XX-D-008 | 1990s DOE Air Toxics Studies | DOE 8 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 69 | 61 | Minnesota Power Company | subbituminous | Northern Great Plains | Montana and Wyoming, Powder River Basin, Rosebud seam | Front-fired | Boswell Energy Center, Unit 2. FF eff. = 99.7%. FF air/colth = 1.97:1 | 5 |  | 899 | 1.199 | mg/Nm3 | Good | 1993-06-27 | SW-846 method 9056 | EPA methods 5/26A | 142000 | dscfm | 27.72 in Hg, 322 deg F, 11.2 % moisture, 14.5/4.8 %CO2/%O2
XX-D-009 | 1990s DOE Air Toxics Studies | Milliken Unit 2 | NOx: LNB, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 150 |  | NYSEG | bituminous | Eastern | Pittsburgh Seam | Tangential | 50/50 mix of raw and cleaned coal. Belco ESP, SHU forced oxidation wet scrubber w/ formic acid addition. CE LNCFS-III low NOx burners. 90-98% S02 removal. 99.9% ESP particulate removal. Heavy metals wastewater treatment facility. | 1 |  | 372 | 0.49 | mg/Nm3 | Acceptable | 1996-08-07 | EPA method 9056 | EPA method 5/8 | 358667 | dscfm | 122 F, 5.66% O2, 13.81% CO2, 14.4% H20 | QA/QC data not available for evaluation.
XX-D-009 | 1990s DOE Air Toxics Studies | Milliken Unit 2 | NOx: LNB, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 150 |  | NYSEG | bituminous | Eastern | Pittsburgh Seam | Tangential | 50/50 mix of raw and cleaned coal. Belco ESP, SHU forced oxidation wet scrubber w/ formic acid addition. CE LNCFS-III low NOx burners. 90-98% S02 removal. 99.9% ESP particulate removal. Heavy metals wastewater treatment facility. | 2 |  | 372 | 0.49 | mg/Nm3 | Acceptable | 1996-08-08 | EPA method 9056 | EPA method 5/8 | 358779 | dscfm | 122 F, 5.52% O2, 13.57% CO2, 14.8% H20 | QA/QC data not available for evaluation.
XX-D-009 | 1990s DOE Air Toxics Studies | Milliken Unit 2 | NOx: LNB, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 150 |  | NYSEG | bituminous | Eastern | Pittsburgh Seam | Tangential | 50/50 mix of raw and cleaned coal. Belco ESP, SHU forced oxidation wet scrubber w/ formic acid addition. CE LNCFS-III low NOx burners. 90-98% S02 removal. 99.9% ESP particulate removal. Heavy metals wastewater treatment facility. | 3 |  | 378 | 0.498 | mg/Nm3 | Acceptable | 1996-08-09 | EPA method 9056 | EPA method 5/8 | 362692 | dscfm | 122 F, 5.76% O2, 13.67% CO2, 14.3% H20 | QA/QC data not available for evaluation.
XX-D-011 | 1990s DOE Air Toxics Studies | DOE 11, Module E | NOx: Unspecified, PM: PS ESPc, SO2: FGDw(Venturi) | Coal-Fired Boilers | 700 | 652 | Tennessee Valley Authority | bituminous | Interior(East, North) | Western KY | Cyclone | Paradise U1. ESP with LS venturi scrubber. Coal washing plant for on-site coal cleaning. Venturi design: 94% part., 84% SO2. ESP eff ~30%. 6 scrubber modules to common stack. Scrubber Module E L/G varied to examine effects on Hg and element removal. | 2 |  | 1850 | 2.161 | mg/Nm3 | Good | 1994-10-25 | CVAA | EPA Method 26A |  |  |  | Converted from chloride to HCl using factor of 1.029
XX-D-011 | 1990s DOE Air Toxics Studies | DOE 11, Module E | NOx: Unspecified, PM: PS ESPc, SO2: FGDw(Venturi) | Coal-Fired Boilers | 700 | 652 | Tennessee Valley Authority | bituminous | Interior(East, North) | Western KY | Cyclone | Paradise U1. ESP with LS venturi scrubber. Coal washing plant for on-site coal cleaning. Venturi design: 94% part., 84% SO2. ESP eff ~30%. 6 scrubber modules to common stack. Scrubber Module E L/G varied to examine effects on Hg and element removal. | 4 |  | 1940 | 2.264 | mg/Nm3 | Good | 1994-10-26 | CVAA | EPA Method 26A |  |  |  | Converted from chloride to HCl using factor of 1.029
XX-D-011 | 1990s DOE Air Toxics Studies | DOE 11, Module E | NOx: Unspecified, PM: PS ESPc, SO2: FGDw(Venturi) | Coal-Fired Boilers | 700 | 652 | Tennessee Valley Authority | bituminous | Interior(East, North) | Western KY | Cyclone | Paradise U1. ESP with LS venturi scrubber. Coal washing plant for on-site coal cleaning. Venturi design: 94% part., 84% SO2. ESP eff ~30%. 6 scrubber modules to common stack. Scrubber Module E L/G varied to examine effects on Hg and element removal. | 6 |  | 1940 | 2.264 | mg/Nm3 | Good | 1994-10-27 | CVAA | EPA Method 26A |  |  |  | Converted from chloride to HCl using factor of 1.029
XX-D-011 | 1990s DOE Air Toxics Studies | DOE 11, Module E | NOx: Unspecified, PM: PS ESPc, SO2: FGDw(Venturi) | Coal-Fired Boilers | 700 | 652 | Tennessee Valley Authority | bituminous | Interior(East, North) | Western KY | Cyclone | Paradise U1. ESP with LS venturi scrubber. Coal washing plant for on-site coal cleaning. Venturi design: 94% part., 84% SO2. ESP eff ~30%. 6 scrubber modules to common stack. Scrubber Module E L/G varied to examine effects on Hg and element removal. | 8 |  | 1940 | 2.264 | mg/Nm3 | Good | 1994-10-28 | CVAA | EPA Method 26A |  |  |  | Converted from chloride to HCl using factor of 1.029
XX-D-012 | 1990s DOE Air Toxics Studies | Blount Unit 9 | NOx: Unspecified, PM: MC ESPc | Coal-Fired Boilers | 58 | 58 | Madison Gas and Electric Company | bituminous | Interior(East, North) | Indiana | Front-fired | Baseline coal only tests. | 6 |  | 8750 | 11.8 | mg/Nm3 | Good | 2000-04-15 | Ion chromatography (IC) | Method 26A | 144 | kscfm | 277F, 8.5% O2, 10.5% CO2, 7.3% mositure | Reported on a 3% O2, ppmv basis. ppmv concentration converted to mg/Nm3 using a factor of 36/23.7 = 1.52
XX-D-012 | 1990s DOE Air Toxics Studies | Blount Unit 9 | NOx: Unspecified, PM: MC ESPc | Coal-Fired Boilers | 58 | 58 | Madison Gas and Electric Company | bituminous | Interior(East, North) | Indiana | Front-fired | Baseline coal only tests. | 4 |  | 19400 | 26.1 | mg/Nm3 | Good | 2000-04-14 | Ion chromatography (IC) | Method 26A | 149 | kscfm | 278F, 9.3% O2, 10.1% CO2, 6.8% mositure | Reported on a 3% O2, ppmv basis. ppmv concentration converted to mg/Nm3 using a factor of 36/23.7 = 1.52
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 9 |  | 478 | 0.664 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 273561 | acfm | 339F, 14.6% CO2, 4.3% O2, 13.98% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 7 |  | 284 | 0.3946 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 257317 | acfm | 327F, 14.6% CO2, 4.3% O2, 13.93% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-D-013 | 1990s DOE Air Toxics Studies | Meramec, Unit 2 | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 140 | 140 | AmerenUE | subbituminous | Northern Great Plains | Powder River Basin | Tangential | ESP SCA 320 ft2/kacfm. | 8 |  | 288 | 0.4001 | mg/Nm3 | Good | 2004-08-26 | Ion chromatography (IC) | EPA Method 26A | 271912 | acfm | 327F, 14.5% CO2, 4.4% O2, 13.98% H2O | Individual run data not reported. Calculated from field sample data sheets and reported analytical data for each run. Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-D-014 | 1990s DOE Air Toxics Studies | Holcomb, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 | 360 | Sunflower Electric | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Niro Joy Western lime SD absorber with Joy Western reverse gas fabric filter. | 1 |  | 15.3 | 0.01784 | mg/Nm3 | Good | 2004-05-18 | Ion chromatography (IC) | EPA Method 26A | 822296 | dscfm | 193.5F, 12.2% CO2, 7.4% O2
XX-D-014 | 1990s DOE Air Toxics Studies | Holcomb, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 | 360 | Sunflower Electric | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Niro Joy Western lime SD absorber with Joy Western reverse gas fabric filter. | 2 |  | 69.3 | 0.08055 | mg/Nm3 | Good | 2004-05-19 | Ion chromatography (IC) | EPA Method 26A | 826784 | dscfm | 190.8F, 12.3% CO2, 7% O2
XX-D-014 | 1990s DOE Air Toxics Studies | Holcomb, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 | 360 | Sunflower Electric | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Niro Joy Western lime SD absorber with Joy Western reverse gas fabric filter. | 4 |  | 42.2 | 0.04905 | mg/Nm3 | Good | 2004-05-20 | Ion chromatography (IC) | EPA Method 26A | 840015 | dscfm | 190.7F, 12.4% CO2, 7.1% O2
XX-FC-010 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 10 | NOx: Unspecified, PM: FFs, SO2: FGDba | Coal-Fired Boilers | 100 |  | Confidential | subbituminous | Rocky Mountain |  | Fluidized bed | Atomopheric FBC with limestone addition for SO2 control. Retest for VOCs in Dec. 1990. Ca/S = 4.0. FF air/cloth = 2.5 acfm/ft2. | 1 |  | 927 | 1.234 | mg/Nm3 | Good | 1990-05-01 | EPA method 300.0 | EPA draft method | 15500000 | dscfh |  | Chloride expressed as HCl by mulplying by 1.028 (36/35).
XX-FC-011 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 11 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River | Tangential | 24 % FGD bypass. A mercury and VOST retest were performed at this site. | 1 |  | 1160 | 1.282 | mg/Nm3 | Acceptable | 1990-08-21 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1788000 | dscfm | 6.9% O2, 18.6% moisture, 186 degrees F
XX-FC-011 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 11 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River | Tangential | 24 % FGD bypass. A mercury and VOST retest were performed at this site. | 2 |  | 1940 | 2.153 | mg/Nm3 | Acceptable | 1990-08-22 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1732000 | dscfm | 6.9% O2, 17.1% moisture, 188 degrees F
XX-FC-011 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 11 | NOx: OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River | Tangential | 24 % FGD bypass. A mercury and VOST retest were performed at this site. | 3 |  | 1150 | 1.281 | mg/Nm3 | Acceptable | 1990-08-23 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1754000 | dscfm | 6.2% O2, 17.2% moisture, 187 degrees F
XX-FC-012 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 12 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | A mercury and VOST retest were performed at this site. | 2 |  | 2710 | 3.07 | mg/Nm3 | Acceptable | 1990-08-01 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1491166 | scfm | 7.0% O2
XX-FC-012 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 12 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | A mercury and VOST retest were performed at this site. | 3 |  | 2550 | 2.89 | mg/Nm3 | Acceptable | 1990-08-02 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1470382 | scfm | 7.0% O2
XX-FC-012 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 12 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | A mercury and VOST retest were performed at this site. | 1 |  | 2170 | 2.45 | mg/Nm3 | Acceptable | 1990-07-31 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1472615 | scfm | 6.3% O2
XX-FC-014 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 14 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | Pilot plant with fluegas slipstream from a 700MW unit. | 1 | < | 838 | 0.981 | mg/Nm3 | Acceptable | 1990-07-25 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 8530 | dscfm
XX-FC-014 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 14 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | Pilot plant with fluegas slipstream from a 700MW unit. | 2 | < | 914 | 1.07 | mg/Nm3 | Acceptable | 1990-07-26 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 8530 | dscfm
XX-FC-014 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 14 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 700 |  | Confidential | bituminous | Eastern | Western Pennsylvania | Wall-fired | Pilot plant with fluegas slipstream from a 700MW unit. | 3 | @ | 2060 | 2.41 | mg/Nm3 | Acceptable | 1990-07-27 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 8530 | dscfm |  | Value is less than five times the detection limit
XX-FC-015 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 15 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 600 |  | Confidential | bituminous | Eastern | Appalachia | Tangential |  | 1 |  | 50300 | 67 | mg/Nm3 | Acceptable | 1990-10-23 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1140000 | dscfm | 12% CO2, 10% O2, 7.49% H2O, 285 deg. F
XX-FC-015 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 15 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 600 |  | Confidential | bituminous | Eastern | Appalachia | Tangential |  | 4 |  | 44300 | 59 | mg/Nm3 | Acceptable | 1990-10-27 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1170000 | dscfm
XX-FC-015 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 15 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 600 |  | Confidential | bituminous | Eastern | Appalachia | Tangential |  | 5 |  | 45800 | 61 | mg/Nm3 | Acceptable | 1990-10-27 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1170000 | dscfm
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 | NOx: OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virgina/Kentucky | Wall-fired | Overfire air test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 96%. | 3 |  | 17200 | 20.93 | mg/Nm3 | Acceptable | 1991-03-05 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1075909 | dscfm | 6.27%H2O, O2=7%
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 | NOx: OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virgina/Kentucky | Wall-fired | Overfire air test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 96%. | 5 |  | 19200 | 23.4 | mg/Nm3 | Acceptable | 1991-03-06 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1075909 | dscfm | 6.27%H2O, O2=7%
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 | NOx: OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virgina/Kentucky | Wall-fired | Overfire air test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 96%. | 4 |  | 17800 | 21.74 | mg/Nm3 | Acceptable | 1991-03-06 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1075909 | dscfm | 6.27%H2O, O2=7%
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 OFA/LNB | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virginia/Kentucky | Wall-fired | Overfire air, low NOx burner test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 98%. | 2 |  | 14700 | 16.95 | mg/Nm3 | Acceptable | 1993-05-19 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1070000 | dscfm | 302 deg. F, 6.7% moisture, 8.8% O2, 10.8% CO2
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 OFA/LNB | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virginia/Kentucky | Wall-fired | Overfire air, low NOx burner test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 98%. | 3 |  | 14700 | 17.01 | mg/Nm3 | Acceptable | 1993-05-20 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1090000 | dscfm | 308 deg. F, 4.9% moisture, 8.0% O2, 11.0% CO2
XX-FC-016 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 16 OFA/LNB | NOx: LNB OFA, PM: ESPc | Coal-Fired Boilers | 500 |  | Confidential | bituminous | Eastern | Virginia/Kentucky | Wall-fired | Overfire air, low NOx burner test conditions. Particulate limit = 0.24 lb/million Btu. ESP eff. = 98%. | 4 |  | 16400 | 18.91 | mg/Nm3 | Acceptable | 1993-05-21 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1080000 | dscfm | 308 deg. F, 6.3% moisture, 8.0% O2, 11.0% CO2
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18 | NOx: Unspecified, PM: MC ESPc(With Conditioning) | Coal-Fired Boilers | 400 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential |  | 1 |  | 18900 | 18.4 | mg/Nm3 | Acceptable | 1992-02-26 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 974506 | dscfm | 8.1% moisture, 265 deg. F, 8.5% O2
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18 | NOx: Unspecified, PM: MC ESPc(With Conditioning) | Coal-Fired Boilers | 400 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential |  | 2 |  | 29900 | 29.2 | mg/Nm3 | Acceptable | 1992-02-27 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 807480 | dscfm | 8.3% moisture, 265 deg. F, 8.0% O2
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18 | NOx: Unspecified, PM: MC ESPc(With Conditioning) | Coal-Fired Boilers | 400 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential |  | 3 |  | 31700 | 30.9 | mg/Nm3 | Acceptable | 1992-02-28 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 910232 | dscfm | 8.0% moisture, 268 deg. F, 8.5% O2
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18FF | NOx: Unspecified, PM: MC ESPc(With Conditioning) FFp | Coal-Fired Boilers | 1 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential | A 1-MW equivalent PJFF draws gas from the outlet of one of the two ESPs. | 1 |  | 20300 | 17.8 | mg/Nm3 | Acceptable | 1992-02-26 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2932 | dscfm
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18FF | NOx: Unspecified, PM: MC ESPc(With Conditioning) FFp | Coal-Fired Boilers | 1 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential | A 1-MW equivalent PJFF draws gas from the outlet of one of the two ESPs. | 2 |  | 34000 | 29.8 | mg/Nm3 | Acceptable | 1992-02-27 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2874 | dscfm
XX-FC-018 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 18FF | NOx: Unspecified, PM: MC ESPc(With Conditioning) FFp | Coal-Fired Boilers | 1 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia | Tangential | A 1-MW equivalent PJFF draws gas from the outlet of one of the two ESPs. | 3 |  | 40000 | 35.1 | mg/Nm3 | Acceptable | 1992-02-28 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2840 | dscfm
XX-FC-019 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 19 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 1200 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia; Martin County, Kentucky | Wall-fired |  | 2 |  | 60100 | 63.7 | mg/Nm3 | Acceptable | 1992-03-11 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2483682 | dscfm | H2O=7.47%, T=278F, O2=7%, CO2=13.5%
XX-FC-019 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 19 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 1200 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia; Martin County, Kentucky | Wall-fired |  | 3 |  | 99100 | 105 | mg/Nm3 | Acceptable | 1992-03-12 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2563494 | dscfm | H2O=7.11%, T=280F, O2=7.5%, CO2=13.5%
XX-FC-019 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 19 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 1200 |  | Confidential | bituminous | Eastern | East Kentucky and West Virginia; Martin County, Kentucky | Wall-fired |  | 4 |  | 64300 | 68.1 | mg/Nm3 | Acceptable | 1992-03-13 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2588796 | dscfm | H2O=6.75%, T=281F, O2=6.25%, CO2=14.0%
XX-FC-020 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 20 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 720 |  | Confidential | lignite | Gulf | Wilcox Group, Harrison County, Texas | Wall-fired | ESP eff. = 99.75%, 5% FGD bypass, 655MW during testing | 3 |  | 190 | 0.1736 | mg/Nm3 | Acceptable | 1993-06-10 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 3100000 | Nm3/hr | 10.0% O2, 18.0% H2O, 11.0% CO2, 135F
XX-FC-020 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 20 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 720 |  | Confidential | lignite | Gulf | Wilcox Group, Harrison County, Texas | Wall-fired | ESP eff. = 99.75%, 5% FGD bypass, 655MW during testing | 2 |  | 75.3 | 0.0686 | mg/Nm3 | Acceptable | 1993-06-09 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 3140000 | Nm3/hr | 10.0% O2, 18.2% H2O, 10.5% CO2, 134F
XX-FC-020 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 20 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 720 |  | Confidential | lignite | Gulf | Wilcox Group, Harrison County, Texas | Wall-fired | ESP eff. = 99.75%, 5% FGD bypass, 655MW during testing | 1 |  | 57.2 | 0.0521 | mg/Nm3 | Acceptable | 1993-06-08 | Ion chromatography (IC), EPA method 300.0 | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 3100000 | Nm3/hr | 10.0% O2, 18.1% H2O, 10.5% CO2, 134F
XX-FC-021 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 21 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 4 |  | Confidential | bituminous | Eastern | Pennsylvania and West Virginia | Tangential | Pilot plant with fluegas slipstream from a 700MW unit. | 5 |  | 2030 | 2.507 | mg/Nm3 | Acceptable | 1992-08-22 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13000 | Nm3/hr |  | Value is less than five times the method detection limit
XX-FC-021 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 21 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 4 |  | Confidential | bituminous | Eastern | Pennsylvania and West Virginia | Tangential | Pilot plant with fluegas slipstream from a 700MW unit. | 4 |  | 2690 | 3.316 | mg/Nm3 | Acceptable | 1992-08-21 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13100 | Nm3/hr |  | Value is less than five times the method detection limit
XX-FC-021 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 21 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 4 |  | Confidential | bituminous | Eastern | Pennsylvania and West Virginia | Tangential | Pilot plant with fluegas slipstream from a 700MW unit. | 3 |  | 2690 | 3.319 | mg/Nm3 | Acceptable | 1992-08-20 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 12900 | Nm3/hr |  | Value is less than five times the method detection limit
XX-FC-021 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 21 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 4 |  | Confidential | bituminous | Eastern | Pennsylvania and West Virginia | Tangential | Pilot plant with fluegas slipstream from a 700MW unit. | 2 |  | 453 | 0.558 | mg/Nm3 | Acceptable | 1992-08-19 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13100 | Nm3/hr
XX-FC-022 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 22 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin, Black Thunder Mine, Smith and Roland Seam, Wyoming | Wall-fired |  | 1 |  | 576 | 0.683 | mg/Nm3 | Acceptable | 1993-07-13 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1540000 | dscfm | 12.75%CO2, 8%O2, 13.0%H2O, 292 deg.F
XX-FC-022 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 22 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin, Black Thunder Mine, Smith and Roland Seam, Wyoming | Wall-fired |  | 2 |  | 731 | 0.867 | mg/Nm3 | Acceptable | 1993-07-14 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1560000 | dscfm | 12.75%CO2, 7.5%O2, 13.6%H2O, 303 deg.F
XX-FC-022 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 22 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 700 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin, Black Thunder Mine, Smith and Roland Seam, Wyoming | Wall-fired |  | 3 |  | 725 | 0.86 | mg/Nm3 | Acceptable | 1993-07-15 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 1590000 | dscfm | 13%CO2, 7.75%O2, 13.6%H2O, 299 deg.F
XX-FC-101R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 101R | NOx: LNB, PM: FFr, SO2: FGDw | Coal-Fired Boilers | 800 | 800 | Confidential | subbituminous | Rocky Mountain | New Mexico | Wall-fired | 25% FGD bypass. Sulfur addition in FGD system. Controlled flow/split flame LNB system. 99.9% particulate removal across FF. Fly ash and FGD solids mixed to form stabilized sludge. Stabilized sludge and bottom ash disposed in an abandoned mine. | 3 |  | 2240 | 2.65 | mg/Nm3 | Good | 1994-01-13 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2600000 | Nm3/hr | 11.8% CO2, 5.3% O2, 82.9% N2, 143 deg. F, 11.3% moisture
XX-FC-101R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 101R | NOx: LNB, PM: FFr, SO2: FGDw | Coal-Fired Boilers | 800 | 800 | Confidential | subbituminous | Rocky Mountain | New Mexico | Wall-fired | 25% FGD bypass. Sulfur addition in FGD system. Controlled flow/split flame LNB system. 99.9% particulate removal across FF. Fly ash and FGD solids mixed to form stabilized sludge. Stabilized sludge and bottom ash disposed in an abandoned mine. | 2 |  | 2780 | 3.29 | mg/Nm3 | Good | 1994-01-12 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2580000 | Nm3/hr | 12.9% CO2, 7.2% O2, 79.9% N2, 135 deg. F, 11.6% moisture
XX-FC-101R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 101R | NOx: LNB, PM: FFr, SO2: FGDw | Coal-Fired Boilers | 800 | 800 | Confidential | subbituminous | Rocky Mountain | New Mexico | Wall-fired | 25% FGD bypass. Sulfur addition in FGD system. Controlled flow/split flame LNB system. 99.9% particulate removal across FF. Fly ash and FGD solids mixed to form stabilized sludge. Stabilized sludge and bottom ash disposed in an abandoned mine. | 1 |  | 2360 | 2.8 | mg/Nm3 | Good | 1994-01-11 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 2550000 | Nm3/hr | 13.3% CO2, 5.8% O2, 80.9% N2, 142 deg. F, 11.5% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110 | NOx: Unspecified, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 2; hot-side only during runs 3, 4, and 5. | 3 |  | 165000 | 218.3 | mg/Nm3 | Acceptable | 1991-09-19 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13873 | m3/min | 7.6% O2, 11% CO2, 9.6% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110 | NOx: Unspecified, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 2; hot-side only during runs 3, 4, and 5. | 4 |  | 160000 | 212 | mg/Nm3 | Acceptable | 1991-09-20 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13465 | m3/min | 8% O2, 12% CO2, 9.5% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110 | NOx: Unspecified, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 2; hot-side only during runs 3, 4, and 5. | 5 |  | 110000 | 145.5 | mg/Nm3 | Acceptable | 1991-09-21 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 14861 | m3/min | 8.8% O2, 11.5% CO2, 9.4% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110 | NOx: Unspecified, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 2; hot-side only during runs 3, 4, and 5. | 2 |  | 111000 | 147.1 | mg/Nm3 | Acceptable | 1991-09-18 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13718 | m3/min | 6.2% O2, 12.5% CO2, 9.7% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110L | NOx: OFA, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 1; hot-side only during runs 2, 3, and 4. | 2 |  | 145000 | 191.4 | mg/Nm3 | Acceptable | 1992-01-15 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13551 | m3/min | 7.5% O2, 11.5% CO2, 7.5% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110L | NOx: OFA, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 1; hot-side only during runs 2, 3, and 4. | 1 |  | 158000 | 208.8 | mg/Nm3 | Acceptable | 1992-01-14 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 13615 | m3/min | 7.0% O2, 11.5% CO2, 8.2% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110L | NOx: OFA, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 1; hot-side only during runs 2, 3, and 4. | 4 |  | 154000 | 204 | mg/Nm3 | Acceptable | 1992-01-17 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 14174 | m3/min | 7.5% O2, 12.0% CO2, 6.9% moisture
XX-FC-110 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 110L | NOx: OFA, PM: ESPhc | Coal-Fired Boilers | 196 |  | Confidential | bituminous | Eastern | Kentucky | Tangential | Unit has a hotside and a coldside ESP. Hot- and cold-side ESP operational during run 1; hot-side only during runs 2, 3, and 4. | 3 |  | 159000 | 210.4 | mg/Nm3 | Acceptable | 1992-01-16 | Ion chromatography (IC) | EPA method 5 w/ H2O2/NaHCO3/Na2CO3 impingers | 14081 | m3/min | 7.5% O2, 11.5% CO2, 7.4% moisture
XX-FC-111 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | subbituminous | Rocky Mountain | Utah/Wyoming | Wall-fired |  | 2 |  | 1140 | 1.07 | mg/Nm3 | Acceptable | 1991-12-17 | Ion chromatography (IC) | Filter, impinger train | 671500 | dscfm | 301 F, 2.5 vol% moisture, 18.8 vol% (dry) O2, 2.0 vol% (dry) CO2
XX-FC-111 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | subbituminous | Rocky Mountain | Utah/Wyoming | Wall-fired |  | 1 |  | 1350 | 1.26 | mg/Nm3 | Acceptable | 1991-12-17 | Ion chromatography (IC) | Filter, impinger train | 607200 | dscfm | 304 F, 9.9 vol% moisture, 5.8 vol% (dry) O2, 13.7 vol% (dry) CO2
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 3 |  | 2370 | 2.607 | mg/Nm3 | Good | 1997-11-12 | EPA method 26 | EPA method 26 | 713091 | dscfm | 262 F, 11% CO2, 7.7% O2, 81.3% N2, 7.4% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 1 |  | 2450 | 2.696 | mg/Nm3 | Good | 1997-11-11 | EPA method 26 | EPA method 26 | 708492 | dscfm | 264 F, 11% CO2, 7.7% O2, 81.3% N2, 7.6% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 1 | NOx: LNB, PM: FF | Coal-Fired Boilers | 275 |  | Confidential | bituminous | Rocky Mountain | Western | Front-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. | 2 |  | 3030 | 3.335 | mg/Nm3 | Good | 1997-11-11 | EPA method 26 | EPA method 26 | 701877 | dscfm | 262.25 F, 11% CO2, 7.7% O2, 81.3% N2, 6.8% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 1 |  | 126 | 0.137 | mg/Nm3 | Good | 1997-11-13 | EPA method 26 | EPA method 26 | 714245 | dscfm | 187.41 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.7% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 3 |  | 70.8 | 0.077 | mg/Nm3 | Good | 1997-11-14 | EPA method 26 | EPA method 26 | 719552 | dscfm | 185.75 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.7% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 4 |  | 103 | 0.112 | mg/Nm3 | Good | 1997-11-14 | EPA method 26 | EPA method 26 | 729618 | dscfm | 185.0 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.8% flue gas moisture
XX-FC-111R | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 111, Unit 2 | NOx: LNB, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 290 |  | Confidential | bituminous | Rocky Mountain | Western | Wall-fired | Design particulate concentration 14 mg/Nm3 (0.005 gr/scf). Zero discharge water system. Air/cloth ratio = 1.7 acf/ft2. SD/FF Ca/S ratio = 1.7. Design SO2 removal 70-76%. | 2 |  | 98.3 | 0.107 | mg/Nm3 | Good | 1997-11-13 | EPA method 26 | EPA method 26 | 706178 | dscfm | 187.25 F, 11.5% CO2, 7.5% O2, 81.0% N2, 11.6% flue gas moisture
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners and overfire air were not used | 3 |  | 4830 | 7.415 | mg/Nm3 | Acceptable | 1992-11-05 | Ion chromatography (IC) | CARB method 421 | 248153 | dscfm | O2=3.32%, NOx=584ppm, SO2=1073ppm
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners and overfire air were not used | 2 |  | 4240 | 6.502 | mg/Nm3 | Acceptable | 1992-11-03 | Ion chromatography (IC) | CARB method 421 | 248078 | dscfm | O2=3.37%, NOx=582ppm, SO2=1640ppm
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners and overfire air were not used | 1 |  | 4300 | 6.588 | mg/Nm3 | Acceptable | 1992-11-02 | Ion chromatography (IC) | CARB method 421 | 247749 | dscfm | O2=2.78%, NOx=572ppm, SO2=1085ppm
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114R | NOx: RB OFA, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners utilized are PC burners, not cyclones | 1 |  | 5350 | 8.138 | mg/Nm3 | Acceptable | 1992-11-04 | Ion chromatography (IC) | CARB method 421 | 233025 | dscfm | O2=2.84%, NOx=277ppm, SO2=1330ppm
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114R | NOx: RB OFA, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners utilized are PC burners, not cyclones | 2 |  | 6730 | 10.25 | mg/Nm3 | Acceptable | 1992-11-04 | Ion chromatography (IC) | CARB method 421 | 247206 | dscfm | O2=2.89%, NOx=274ppm, SO2=1110ppm
XX-FC-114 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 114R | NOx: RB OFA, PM: ESPc | Coal-Fired Boilers | 100 |  | Confidential | bituminous | Interior(East, North) | Indiana Lamar | Cyclone | Reburners utilized are PC burners, not cyclones | 3 |  | 6210 | 9.457 | mg/Nm3 | Acceptable | 1992-11-06 | Ion chromatography (IC) | CARB method 421 | 231039 | dscfm | O2=2.63%, NOx=282ppm, SO2=1048ppm
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115 | NOx: OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na injection to FF for SO2 control. FF eff. = 99.96% | 7 |  | 376 | 0.431 | mg/Nm3 | Acceptable | 1992-11-19 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 414600 | Nm3/hr | 5.65% O2, 12.69% CO2, 7.6% H2O, 262F
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115 | NOx: OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na injection to FF for SO2 control. FF eff. = 99.96% | 1 |  | 922 | 1.056 | mg/Nm3 | Acceptable | 1992-11-17 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 387900 | Nm3/hr | 5.57% O2, 12.93% CO2, 7.3% H2O, 264F
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115 | NOx: OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na injection to FF for SO2 control. FF eff. = 99.96% | 4 |  | 827 | 0.947 | mg/Nm3 | Acceptable | 1992-11-18 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 399100 | Nm3/hr | 5.69% O2, 13.23% CO2, 7.6% H2O, 263F
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115-Urea | NOx: SNCR LNB OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na, injection to FF for SO2 control. FF eff. = 99.98%. Urea injection test. | 1 |  | 701 | 0.83 | mg/Nm3 | Acceptable | 1993-03-10 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 396600 | Nm3/hr | 5.93% O2, 13.63% CO2, 7.9% H2O, 260F
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115-Urea | NOx: SNCR LNB OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na, injection to FF for SO2 control. FF eff. = 99.98%. Urea injection test. | 2 |  | 711 | 0.841 | mg/Nm3 | Acceptable | 1993-03-10 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 411100 | Nm3/hr | 6.12% O2, 13.41% CO2, 7.9% H2O, 262F
XX-FC-115 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 115-Urea | NOx: SNCR LNB OFA, PM: FF, SO2: FGDdsi | Coal-Fired Boilers | 117 | 104 | Confidential | bituminous | Rocky Mountain | Western | Top-fired | Ca, Na, injection to FF for SO2 control. FF eff. = 99.98%. Urea injection test. | 4 |  | 840 | 0.994 | mg/Nm3 | Acceptable | 1993-03-11 | Ion chromatography (IC), EPA method 300.0 | CARB method 421 | 414700 | Nm3/hr | 6.41% O2, 13.21% CO2, 7.7% H2O, 257F
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 160 | 153 | Confidential | bituminous | Eastern | Ohio | Wall-fired | ESP eff. = 99.4% | 1 |  | 31200 | 38.09 | mg/Nm3 | Acceptable | 1993-04-26 | Ion chromatography (IC) | EPA method 26A | 377102 | dscfm | T=321F, moisture=7.7%,velocity=23.8m/s
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 160 | 153 | Confidential | bituminous | Eastern | Ohio | Wall-fired | ESP eff. = 99.4% | 8 |  | 31600 | 38.52 | mg/Nm3 | Acceptable | 1993-05-02 | Ion chromatography (IC) | EPA method 26A | 376495 | dscfm | T=321F, moisture=7.7%,velocity=23.8m/s
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 160 | 153 | Confidential | bituminous | Eastern | Ohio | Wall-fired | ESP eff. = 99.4% | 7 |  | 34700 | 42.28 | mg/Nm3 | Acceptable | 1993-05-01 | Ion chromatography (IC) | EPA method 26A | 373826 | dscfm | T=321F, moisture=7.7%,velocity=23.8m/s
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116-SNRB | NOx: SNRB RB, PM: FF, SO2: FGDsnrb | Coal-Fired Boilers | 5 |  | Confidential | bituminous | Eastern | Ohio | Wall-fired | The coal data associated with this unit are under FCEM 116. Pilot-scale 5 ME equivelant SNRB demonstration. | 8 |  | 285 | 0.3562 | mg/Nm3 | Acceptable | 1993-05-02 | Ion chromatography (IC) | EPA method 26A | 9649 | dscfm | O2=5.55%, SO2=252ppm, NOx=30.5ppm, T=793F, moisture=7.1%, velocity=16.0m/s
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116-SNRB | NOx: SNRB RB, PM: FF, SO2: FGDsnrb | Coal-Fired Boilers | 5 |  | Confidential | bituminous | Eastern | Ohio | Wall-fired | The coal data associated with this unit are under FCEM 116. Pilot-scale 5 ME equivelant SNRB demonstration. | 1 |  | 763 | 0.9539 | mg/Nm3 | Acceptable | 1993-04-26 | Ion chromatography (IC) | EPA method 26A | 9809 | dscfm | O2=5.75%, SO2=207ppm, NOx=42ppm, T=793F, moisture=7.1%, velocity=16.0m/s
XX-FC-116 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 116-SNRB | NOx: SNRB RB, PM: FF, SO2: FGDsnrb | Coal-Fired Boilers | 5 |  | Confidential | bituminous | Eastern | Ohio | Wall-fired | The coal data associated with this unit are under FCEM 116. Pilot-scale 5 ME equivelant SNRB demonstration. | 7 |  | 910 | 1.137 | mg/Nm3 | Acceptable | 1993-05-01 | Ion chromatography (IC) | EPA method 26A | 10078 | dscfm | O2=5.67%, SO2=250ppm, NOx=29ppm, T=793F, moisture=7.1%, velocity=16.0m/s
XX-FC-122 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 122 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 273 | 249 | Confidential | bituminous | Interior(East, North) | Illinois, Saline Co. Big Ridge Mine, Illinois No. 5 Seam | Cyclone | ESP eff. 93-94%. | 3 |  | 226000 | 364 | mg/Nm3 | Good | 1993-05-06 | Ion chromatography (IC) | EPA method 5, train with solution of NaHCO3, Na2CO3, H2O2 | 635000 | dscfm | 1.011 atm, 311 F
XX-FC-122 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 122 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 273 | 249 | Confidential | bituminous | Interior(East, North) | Illinois, Saline Co. Big Ridge Mine, Illinois No. 5 Seam | Cyclone | ESP eff. 93-94%. | 2 |  | 220000 | 354 | mg/Nm3 | Good | 1993-05-05 | Ion chromatography (IC) | EPA method 5, train with solution of NaHCO3, Na2CO3, H2O2 | 646000 | dscfm | 1.009 atm, 313 F
XX-FC-122 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 122 | NOx: Unspecified, PM: ESPc | Coal-Fired Boilers | 273 | 249 | Confidential | bituminous | Interior(East, North) | Illinois, Saline Co. Big Ridge Mine, Illinois No. 5 Seam | Cyclone | ESP eff. 93-94%. | 1 |  | 215000 | 346 | mg/Nm3 | Good | 1993-05-04 | Ion chromatography (IC) | EPA method 5, train with solution of NaHCO3, Na2CO3, H2O2 | 623000 | dscfm | 1.003 atm, 311 F
XX-FC-125 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 125 | PM: PS ESPc, SO2: FGDw(Venturi,Forced ox) | Coal-Fired Boilers | 646 | 630 | Confidential | bituminous | Interior(East, North) | Western Kentucky | Cyclone | Very low ESP efficiency (approx. 30%). Non-representative sample location at FGD inlet prevented evaluation of ESP efficiency and trace substance removals. Limestone venturi scrubber w/ forced oxidation for SO2 control. | 3 |  | 1130 | 1.7 | mg/Nm3 | Good | 1993-08-19 | Ion chromatography (IC) | EPA method 5, filter and solution of NaHCO3, Na2CO3, H2O2 | 1523000 | dscfm | 0.985 atm, 139 F, 16.1% moisture, 7.1% O2 | Only the vapor phase concentrations were calculated, no solid phase data or total data was available.
XX-FC-125 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 125 | PM: PS ESPc, SO2: FGDw(Venturi,Forced ox) | Coal-Fired Boilers | 646 | 630 | Confidential | bituminous | Interior(East, North) | Western Kentucky | Cyclone | Very low ESP efficiency (approx. 30%). Non-representative sample location at FGD inlet prevented evaluation of ESP efficiency and trace substance removals. Limestone venturi scrubber w/ forced oxidation for SO2 control. | 1 |  | 1280 | 1.93 | mg/Nm3 | Good | 1993-08-17 | Ion chromatography (IC) | EPA method 5, filter and solution of NaHCO3, Na2CO3, H2O2 | 1467000 | dscfm | 0.985 atm, 139 F, 15.9% moisture, 6.5% O2 | Only the vapor phase concentrations were calculated, no solid phase data or total data was available.
XX-FC-125 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 125 | PM: PS ESPc, SO2: FGDw(Venturi,Forced ox) | Coal-Fired Boilers | 646 | 630 | Confidential | bituminous | Interior(East, North) | Western Kentucky | Cyclone | Very low ESP efficiency (approx. 30%). Non-representative sample location at FGD inlet prevented evaluation of ESP efficiency and trace substance removals. Limestone venturi scrubber w/ forced oxidation for SO2 control. | 2 |  | 1260 | 1.9 | mg/Nm3 | Good | 1993-08-18 | Ion chromatography (IC) | EPA method 5, filter and solution of NaHCO3, Na2CO3, H2O2 | 1407000 | dscfm | 0.984 atm, 140 F, 16% moisture, 6.8% O2 | Only the vapor phase concentrations were calculated, no solid phase data or total data was available.
XX-FC-126 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 126 | NOx: SCR LNB OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 590 | 590 | Confidential | bituminous | Unknown | Polland, Columbia | Wall-fired | Finland power plant. 0.05 lb/million Btu particulate limit. ESP eff. = 99.5%. ESP SCA = 386 ft2/acfm. Zero FGD flue gas bypass. SCR catalyst upstream of ESP. WWT sludge filter cake from FGD blowdown treatment mixed with coal and reburned during test. | 1 |  | 4370 | 5.11 | mg/Nm3 | Good | 1994-04-14 | Ion chromatography (IC) | Modified Method 5 w/ carbonate, bicarbonate, peroxide | 1742000 | Nm3/hr | 77 C, 5.1 % O2, 14.1% CO2
XX-FC-126 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 126 | NOx: SCR LNB OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 590 | 590 | Confidential | bituminous | Unknown | Polland, Columbia | Wall-fired | Finland power plant. 0.05 lb/million Btu particulate limit. ESP eff. = 99.5%. ESP SCA = 386 ft2/acfm. Zero FGD flue gas bypass. SCR catalyst upstream of ESP. WWT sludge filter cake from FGD blowdown treatment mixed with coal and reburned during test. | 2 |  | 4590 | 5.37 | mg/Nm3 | Good | 1994-04-15 | Ion chromatography (IC) | Modified Method 5 w/ carbonate, bicarbonate, peroxide | 1728000 | Nm3/hr | 77 C, 5.0 % O2, 14.3% CO2
XX-FC-126 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 126 | NOx: SCR LNB OFA, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 590 | 590 | Confidential | bituminous | Unknown | Polland, Columbia | Wall-fired | Finland power plant. 0.05 lb/million Btu particulate limit. ESP eff. = 99.5%. ESP SCA = 386 ft2/acfm. Zero FGD flue gas bypass. SCR catalyst upstream of ESP. WWT sludge filter cake from FGD blowdown treatment mixed with coal and reburned during test. | 3 |  | 4320 | 5.05 | mg/Nm3 | Good | 1994-04-18 | Ion chromatography (IC) | Modified Method 5 w/ carbonate, bicarbonate, peroxide | 1690000 | Nm3/hr | 78 C, 4.8 % O2, 14.5% CO2
XX-FC-131 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 131, Project 3 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 |  | Confidential | Unknown | Unknown | United Kingdom | Wall-fired | Power plant in the United Kingdom. Project 3 with improved ESPs and new wet limestone FGD scrubbers. Fuel blend from multiple sources. | 1 |  | 4700 | 5.5 | mg/Nm3 | Good | 1994-05-11 | Titrimetry | ISO 9096 | 727 | m3/sec | 5.2 % O2
XX-FC-131 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 131, Project 3 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 |  | Confidential | Unknown | Unknown | United Kingdom | Wall-fired | Power plant in the United Kingdom. Project 3 with improved ESPs and new wet limestone FGD scrubbers. Fuel blend from multiple sources. | 5 |  | 5900 | 6.9 | mg/Nm3 | Good | 1994-05-13 | Titrimetry | ISO 9096 | 730 | m3/sec | 5.4 % O2
XX-FC-131 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM 131, Project 3 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 |  | Confidential | Unknown | Unknown | United Kingdom | Wall-fired | Power plant in the United Kingdom. Project 3 with improved ESPs and new wet limestone FGD scrubbers. Fuel blend from multiple sources. | 3 |  | 6330 | 7.4 | mg/Nm3 | Good | 1994-05-12 | Titrimetry | ISO 9096 | 727 | m3/sec | 5.6 % O2
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 1 |  | 561 | 0.562 | mg/Nm3 | Acceptable | 1998-10-15 | unknown | EPA method 26 | 3081476 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 2 |  | 1070 | 1.074 | mg/Nm3 | Acceptable | 1998-10-16 | unknown | EPA method 26 | 3079853 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 4 |  | 663 | 0.664 | mg/Nm3 | Acceptable | 1998-10-17 | unknown | EPA method 26 | 3100494 | dscfm
XX-FC-E29 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | FCEM E29 | NOx: Unspecified, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 1330 |  | Confidential | bituminous | Eastern | OH, Pittsburgh No. 8 | Unknown | 301 validation testing of Ontario Hydro mercury speciation tests. FGD inlet and stack measured. M29 and Semtech Hg CEM also used to for comparison. FGD SO2 removal 93.8 to 94.6%. | 5 |  | 957 | 0.959 | mg/Nm3 | Acceptable | 1998-10-17 | unknown | EPA method 26 | 3140168 | dscfm
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 7 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-06-28 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 11 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-06-30 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 8 |  | 39 | 0.04557 | mg/Nm3 | Good | 2002-06-28 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 13 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-07-01 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 12 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-06-30 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 5 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-06-27 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1 | NOx: LNB, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Lime SD absorber plus reverse air fabric filter. Variable load 300 - 370 MW during tests. | 6 | < | 13 | 0.01519 | mg/Nm3 | Good | 2002-06-27 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1, FF | NOx: LNB, PM: FFr | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SD absorber out of service. Reverse air fabric filter only. Variable load 300 - 370 MW during tests. | 10 |  | 688 | 0.8051 | mg/Nm3 | Good | 2002-06-29 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-L4 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Holcomb 2002, Unit 1, FF | NOx: LNB, PM: FFr | Coal-Fired Boilers | 360 |  | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SD absorber out of service. Reverse air fabric filter only. Variable load 300 - 370 MW during tests. | 9 |  | 455 | 0.5316 | mg/Nm3 | Good | 2002-06-29 | Ion chromatography (IC) | EPA Method 26A |  |  |  | Reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 11 |  | 2470 | 3.477 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 11 |  | 3580 | 5.032 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 9 |  | 2960 | 4.163 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 10 |  | 3590 | 5.043 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 9 |  | 3200 | 4.496 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC10 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | DM, SCR | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Interior(East, North) | Illinois | Tangential | SCR/ESP/Limestone forced oxidation FGD. Research-Cotrell double loop FGD. CERAM SCR catalyst. SV = 3000hr-1, Volume = 499 m2/m3 | 10 |  | 2890 | 4.067 | mg/Nm3 | Acceptable | 2007-06-07 | EPA Method 26, IC | EPA Method 26 | 13266954 | dscfh |  | Overall plant mass balance 252%.
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 3 |  | 2340 | 2.741 | mg/Nm3 | Good | 2008-08-13 | Ion chromatography (IC) | Method 26A | 161013000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 4 |  | 660 | 0.7717 | mg/Nm3 | Good | 2008-08-13 | Ion chromatography (IC) | Method 26A | 161013000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC12 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site E, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox), SO3: SI | Coal-Fired Boilers | 200 | 200 | Confidential | bituminous | Eastern |  | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. Hydrocyclones for FGD solids dewatering. Trona injection immediately upstream of the ESP for SO3 control. | 1 |  | 808 | 0.9445 | mg/Nm3 | Good | 2008-08-12 | Ion chromatography (IC) | Method 26A | 165743000 | dscfh |  | Reported gas concentrations were adjusted from 20C (std cubic meters) to 0C (normal cubic meters).
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 25 | < | 12.6 | 0.01477 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 26 | < | 12.6 | 0.01477 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC13 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site F, Unit 1 | NOx: SCR, PM: ESPc, SO2: FGDw(Forced ox) | Coal-Fired Boilers | 650 | 650 | Confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | SCR/ESP/wet limestone FGD configuration with forced oxidation. | 27 | < | 12.6 | 0.01477 | mg/Nm3 | Good | 2007-04-30 | Ion chromatography (IC) | EPA Method 26A |  |  | 157 deg F | Concentration reported as ppmv. Converted to mg/Nm3 using ideal gas law and MW of compound. DL estimated from raw analytical data and reported instrument MDL.
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 2 |  | 787 | 0.92 | mg/Nm3 | Good | 2006-02-16 | Ion chromatography (IC) | EPA Method 26A
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 9 |  | 436 | 0.51 | mg/Nm3 | Good | 2006-02-17 | Ion chromatography (IC) | EPA Method 26A
XX-FC-SC14 | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | Site G, Unit 7 | NOx: LNB, PM: ESPc, SO2: FGDw | Coal-Fired Boilers | 500 | 500 | Confidential | bituminous | Eastern |  | Tangential | ESP Wet Limestone FGD configuration with (SCR out of service). | 1 |  | 1570 | 1.84 | mg/Nm3 | Good | 2006-02-16 | Ion chromatography (IC) | EPA Method 26A
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | A1, Unit A, baseline | NOx: LNB, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 500 | 487 | confidential | subbit/bit | Northern Great Plains, Eastern | Powder River, Eastern blend | Wall-fired | Unit A, 50:50 blend of PRB and Eastern bituminous coal. ESP with SO3 and NH3 injection for improved particulate control. ESP eff = 98-99.8%. SCA = 240 ft2/1000 acf. Design temp. 244 F. | 3 |  | 48100 | 56.3 | mg/Nm3 | Acceptable | 2001-04-06 | Ion chromatography (IC) | EPA Method 26A |  |  | 13.5% CO2, 4.5% O2 | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | A1, Unit B, baseline | NOx: LNB, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 500 | 403 | confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Unit B, 100% PRB coal. ESP with SO3 and NH3 injection for improved particulate control. ESP eff = 99.6%. SCA = 240 ft2/1000 acf. Design temp. 244 F. | 1 |  | 6580 | 7.7 | mg/Nm3 | Acceptable | 2001-04-09 | Ion chromatography (IC) | EPA Method 26A |  |  | 13.5% CO2, 4.5% O2 | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | A1, Unit B, baseline | NOx: LNB, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 500 | 403 | confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Unit B, 100% PRB coal. ESP with SO3 and NH3 injection for improved particulate control. ESP eff = 99.6%. SCA = 240 ft2/1000 acf. Design temp. 244 F. | 2 |  | 7520 | 8.8 | mg/Nm3 | Acceptable | 2001-04-10 | Ion chromatography (IC) | EPA Method 26A |  |  | 13.5% CO2, 4.7% O2 | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | A1, Unit B, no NH3 | NOx: LNB, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 500 | 445 | confidential | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Unit B, 100% PRB coal. ESP with SO3 for improved particulate control. NH3 injection turned off to observe effects on mercury speciation and control. ESP eff = 99.2-99.8%. SCA = 240 ft2/1000 acf. Design temp. 244 F. | 1 |  | 4450 | 5.2 | mg/Nm3 | Acceptable | 2001-04-10 | Ion chromatography (IC) | EPA Method 26A |  |  | 13.5% CO2, 4.4% O2 | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | S1, SCR | NOx: SCR, PM: ESPc | Coal-Fired Boilers | 650 | 537 | confidential | subbituminous | Northern Great Plains | Power River Basin | Cyclone | SCR catalyst: Cormetech, honeycomb, 1800 hr-1 space velocity, NH3/NOx molar ratio = 1, 8000 hrs operation prior to test, NOx removal = 88.6% avg. ESP: SCA = 323 ft2/1000 acfm, Eff = 99.43%, design temp 320F. Load varied from 500-575MW during tests. | 1 |  | 2050 | 2.4 | mg/Nm3 | Acceptable | 2001-06-05 | Ion chromatography (IC) | EPA Method 26A |  |  | 296 F | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-FC-SCR | EPRI-Sponsored Field Chemical Emission (FCEM) Studies | S1, SCR | NOx: SCR, PM: ESPc | Coal-Fired Boilers | 650 | 537 | confidential | subbituminous | Northern Great Plains | Power River Basin | Cyclone | SCR catalyst: Cormetech, honeycomb, 1800 hr-1 space velocity, NH3/NOx molar ratio = 1, 8000 hrs operation prior to test, NOx removal = 88.6% avg. ESP: SCA = 323 ft2/1000 acfm, Eff = 99.43%, design temp 320F. Load varied from 500-575MW during tests. | 2 |  | 2390 | 2.8 | mg/Nm3 | Acceptable | 2001-06-05 | Ion chromatography (IC) | EPA Method 26A |  |  | 296 F | Reported as ppmv total chlorides. Converted to mg/Nm3 HCl using MW = 36.4. Reported on a 3% O2 basis.
XX-IC-023 | 1999 Utility Mercury Information Collection Request | Duck Creek Station | NOx: LNB, PM: ESPc, SO2: FGDw(Natural ox) | Coal-Fired Boilers | 400 | 375 | Central Illinois Light Company | bituminous | Eastern |  | Wall-fired | Sampled in 1998 prior to EPA ICR. ESP eff = 99.8%, 83% SO2 removal in natural oxidation FGD scrubber. NOx Core LNB system. Outlet samples collected at the outlet of the FGD scrubber rather than stack. No indication of FGD bypass in report. | 1 |  | 3150 | 4.6 | mg/Nm3 | Good | 1999-07-14 | Method 26 | Mod EPA Method 26 | 869600 | dscfm |  | Data are taken from the EPA ICR spreadsheet dated June 2001 (www.epa.gov/ttn/atw/combust/utiltox/utoxpg.html#DA3). Converted from ppmv to mg/Nm3 as ppmv*(MW/23.7)
XX-IC-023 | 1999 Utility Mercury Information Collection Request | Duck Creek Station | NOx: LNB, PM: ESPc, SO2: FGDw(Natural ox) | Coal-Fired Boilers | 400 | 375 | Central Illinois Light Company | bituminous | Eastern |  | Wall-fired | Sampled in 1998 prior to EPA ICR. ESP eff = 99.8%, 83% SO2 removal in natural oxidation FGD scrubber. NOx Core LNB system. Outlet samples collected at the outlet of the FGD scrubber rather than stack. No indication of FGD bypass in report. | 2 |  | 2060 | 3 | mg/Nm3 | Good | 1999-07-15 | Method 26 | Mod EPA Method 26 | 875300 | dscfm |  | Data are taken from the EPA ICR spreadsheet dated June 2001 (www.epa.gov/ttn/atw/combust/utiltox/utoxpg.html#DA3). Converted from ppmv to mg/Nm3 as ppmv*(MW/23.7)
XX-IC-023 | 1999 Utility Mercury Information Collection Request | Duck Creek Station | NOx: LNB, PM: ESPc, SO2: FGDw(Natural ox) | Coal-Fired Boilers | 400 | 375 | Central Illinois Light Company | bituminous | Eastern |  | Wall-fired | Sampled in 1998 prior to EPA ICR. ESP eff = 99.8%, 83% SO2 removal in natural oxidation FGD scrubber. NOx Core LNB system. Outlet samples collected at the outlet of the FGD scrubber rather than stack. No indication of FGD bypass in report. | 3 |  | 2060 | 3 | mg/Nm3 | Good | 1999-07-16 | Method 26 | Mod EPA Method 26 | 853400 | dscfm |  | Data are taken from the EPA ICR spreadsheet dated June 2001 (www.epa.gov/ttn/atw/combust/utiltox/utoxpg.html#DA3). Converted from ppmv to mg/Nm3 as ppmv*(MW/23.7)
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 1 |  | 340 | 0.3633 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 330309.9034 | ng/dscm | 0.00033986 |  | 1 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 2 |  | 293 | 0.3104 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 282154.6187 | ng/dscm | 0.00029267 |  | 2 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 3 |  | 444 | 0.4637 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 421550.2844 | ng/dscm | 0.00044449 |  | 3 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 1 |  | 472 | 0.5735 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 521337.9605 | ng/dscm | 0.00047174 |  | 1 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 2 |  | 521 | 0.6194 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 563110.0534 | ng/dscm | 0.00052061 |  | 2 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 3 |  | 406 | 0.4971 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 451941.3767 | ng/dscm | 0.00040606 |  | 3 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 |  | 3010 | 4.021 | mg/Nm3 | Unknown | 2010-04-05 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3655216.6139 | ng/dscm | 0.0030087 |  | 1 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 |  | 2930 | 3.911 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3555859.2254 | ng/dscm | 0.0029269 |  | 2 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 |  | 2750 | 3.649 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3317663.3714 | ng/dscm | 0.0027486 |  | 3 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 |  | 1880 | 2.233 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 2030211.0295 | ng/dscm | 0.001877 |  | 1 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 |  | 1660 | 2.003 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 1820545.5275 | ng/dscm | 0.0016591 |  | 2 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 |  | 1950 | 2.349 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 2135765.2558 | ng/dscm | 0.0019464 |  | 3 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 138 | 0.1413 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 128464.215 | ng/dscm | 0.00013773 |  | 1 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 174 | 0.1595 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 140890.8728 | ng/dscm | 0.000174 |  | 2 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 | < | 165 | 0.1518 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 133946.3273 | ng/dscm | 0.000165 | <301 | 3 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 187 | 0.192 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 174505.622 | ng/dscm | 0.00018709 |  | 1 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 152 | 0.1597 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 145168.0852 | ng/dscm | 0.00015181 |  | 2 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 148 | 0.1561 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 141932.0196 | ng/dscm | 0.00014843 |  | 3 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 | < | 113 | 0.1448 | mg/Nm3 | Unknown | 2010-07-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 131674.4376 | ng/dscm | 0.00011275 | [<375] | 1 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 | < | 88.1 | 0.1207 | mg/Nm3 | Unknown | 2010-07-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 109755.8699 | ng/dscm | 8.807e-05 | [<313] | 2 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 | < | 105 | 0.1219 | mg/Nm3 | Unknown | 2010-07-30 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 110826.8834 | ng/dscm | 0.00010474 | [<315] | 3 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 | < | 100 | 0.1321 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 120059.0565 | ng/dscm | 0.00010012 | [<297] | 1 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 | < | 92.5 | 0.1212 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 110198.0179 | ng/dscm | 9.2497e-05 | [<323] | 2 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 | < | 95.3 | 0.1224 | mg/Nm3 | Unknown | 2010-07-28 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 111279.143 | ng/dscm | 9.5285e-05 | [<345] | 3 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 3070 | 4.445 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4040870.6429 | ng/dscm | 0.0030688 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 3520 | 5.124 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4658345.5573 | ng/dscm | 0.0035168 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 3210 | 4.732 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4301557.1123 | ng/dscm | 0.0032094 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 3070 | 4.445 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4040870.6429 | ng/dscm | 0.0030688 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 3520 | 5.124 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4658345.5573 | ng/dscm | 0.0035168 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 3210 | 4.732 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4301557.1123 | ng/dscm | 0.0032094 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 1 |  | 16100 | 23.24 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21130917.4799 | ng/dscm | 0.016144 |  | 1 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 2 |  | 16400 | 23.15 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21042912.6053 | ng/dscm | 0.01637 |  | 2 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 3 |  | 14400 | 20.8 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 18913247.8355 | ng/dscm | 0.014363 |  | 3 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 10300 | 12.05 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 10954028.1986 | ng/dscm | 0.010302 |  | 1 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 26600 | 31.26 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 28417639.5337 | ng/dscm | 0.026606 |  | 2 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 24000 | 28.15 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 25589074.037 | ng/dscm | 0.024012 |  | 3 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 30800 | 36.72 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 33386037.8785 | ng/dscm | 0.030809 |  | 1 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 36000 | 41.5 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 37730723.7419 | ng/dscm | 0.035977 |  | 2 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 32600 | 37.58 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 34167419.0636 | ng/dscm | 0.032614 |  | 3 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 1 |  | 432 | 0.5708 | mg/Nm3 | Unknown | 2010-06-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 518877.4387 | ng/dscm | 0.00043213 | Run 1 = 2.42 ug/ml, Blank = 0.928 ug/ml, Vol = 1091 - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 1 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 2 |  | 124 | 0.1655 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 150472.7526 | ng/dscm | 0.00012387 | Run 2 = 1.37ug/ml, Blank = 0.928 ug/ml, Vol = 1051 ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 2 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 3 |  | 96.6 | 0.1259 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 114484.1333 | ng/dscm | 9.6586e-05 | Run 3 = 1.24ug/ml, Blank = 0.928ug/ml, Vol = 1116ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 3 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 1 |  | 22400 | 29.57 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 26882486.9724 | ng/dscm | 0.022384 | Run 1 = 82.5ug/ml, Blank = [ | 1 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 2 |  | 1510 | 1.942 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1765815.221 | ng/dscm | 0.0015078 | Run 2 = 5.86ug/ml, Blank = [ | 2 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 3 |  | 310 | 0.3794 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 344904.8208 | ng/dscm | 0.00030995 | Run 3 = 2.34ug/ml, Blank = 1.59ug/ml, Vol = 1369 ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit." | 3 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 4 |  | 399 | 0.5358 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 487049.3707 | ng/dscm | 0.00039946 | Run 4 = 2.74ug/ml, Blank = 1.59ug/ml, Vol = 1270ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit." | 4 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 7210 | 9.379 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 8526442.9751 | ng/dscm | 0.0072143 | 26361, Blank N/D | 2 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 4430 | 5.799 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5272165.2859 | ng/dscm | 0.0044343 | 16234, Blank N/D | 3 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 6760 | 8.639 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 7853282.4702 | ng/dscm | 0.0067582 | 32174, Blank N/D | 1 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 1 |  | 600 | 0.7428 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.3558 | ng/dscm | 0.00060024 | HCl 2360, Blank 266 | 1 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 2 |  | 601 | 0.7387 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 671563.0597 | ng/dscm | 0.00060077 | HCl 2400, Blank 266 | 2 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 3 |  | 525 | 0.6465 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 587726.0108 | ng/dscm | 0.00052458 | HCl 2130, Blank 266 | 3 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 1 |  | 600 | 0.7428 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.3558 | ng/dscm | 0.00060024 | HCl 2360, Blank 266 | 1 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 2 |  | 601 | 0.7387 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 671563.0597 | ng/dscm | 0.00060077 | HCl 2400, Blank 266 | 2 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 3 |  | 525 | 0.6465 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 587726.0108 | ng/dscm | 0.00052458 | HCl 2130, Blank 266 | 3 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 5 |  | 752 | 0.9609 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 873511.378 | ng/dscm | 0.000752 | 700, 239 | M26A-5 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 4 |  | 832 | 1.065 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 967835.2236 | ng/dscm | 0.00083152 | 892, 159 - backup impinger amount was coded "B" indicating the amount detected was a positive result less than the reporting limit but greater than the MDL. | M26A-4 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 317 | 0.4052 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | BDL | 368337.7846 | ng/dscm | 0.0003171 | [ | M26A-3 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 4 | UNK | 1040 | 1.413 | mg/Nm3 | Poor | 2010-04-22 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1284749.447 | ng/dscm | 0.0010374 |  | 4 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 9170 | 10.99 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 9988333.698 | ng/dscm | 0.0091681 |  | 1 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 1160 | 1.442 | mg/Nm3 | Poor | 2010-04-22 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1310995.8666 | ng/dscm | 0.0011615 |  | 3 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 7560 | 7.755 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 7050038.887 | ng/dscm | 0.0075586 |  | 2 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 5320 | 6.379 | mg/Nm3 | Poor | 2010-03-11 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 5798764.6844 | ng/dscm | 0.0053225 |  | 3 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 6140 | 6.295 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 5722344.4939 | ng/dscm | 0.0061352 |  | 1 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 1 |  | 60.6 | 0.06967 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 523536 | dscfm | 6.23 % O2, 60.83 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.0441 | ppmv | 0.0022 |  | 2017-01-01 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 2 |  | 65.5 | 0.0752 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 523536 | dscfm | 6.23 % O2, 62.46 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.0476 | ppmv | 0.0003 |  | 2017-01-02 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 3 | < | 70.1 | 0.08057 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 528024 | dscfm | 6.29 % O2, 60.08 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.051 | ppmv | 0.0001 |  | 2017-01-03 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 |  | 990 | 1.237 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1124798.6213 | ng/dscm | 0.00098971 |  | M26A-1 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 1030 | 1.292 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1174558.1518 | ng/dscm | 0.0010335 |  | M26A-2 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 |  | 1000 | 1.192 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | EPA method 26 | 369719 | dscfm | 16.98 % moisture, 13.1 % CO2, 6.4 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.75436 | ppmv | 0.001 | [200] | 1 | 90000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 1000 | 1.245 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | EPA method 26 | 391635 | dscfm | 16.97 % moisture, 13 % CO2, 6.4 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.78775 | ppmv | 0.001 | [200] | 2 | 90000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 535 | 0.6749 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 613553.9487 | ng/dscm | 0.0005347 | [<1600] | 1 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 497 | 0.6228 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 566182.9141 | ng/dscm | 0.00049679 | [<1500] | 2 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 507 | 0.6393 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 581214.2089 | ng/dscm | 0.00050651 | [<1500] | 3 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 224 | 0.2533 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 230232.9558 | ng/dscm | 0.00022423 |  | 1 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 137 | 0.1583 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 143952.0742 | ng/dscm | 0.00013706 |  | 2 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 106 | 0.1212 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 110194.1899 | ng/dscm | 0.00010571 |  | 3 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 228 | 0.2841 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 258235.4631 | ng/dscm | 0.00022801 |  | 1 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 269 | 0.3254 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 295806.3528 | ng/dscm | 0.00026861 |  | 2 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 252 | 0.3075 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 279510.7914 | ng/dscm | 0.00025202 |  | 3 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 103 | 0.1289 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 117139.1492 | ng/dscm | 0.00010343 |  | 1 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 81.9 | 0.1024 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 93081.4658 | ng/dscm | 8.1902e-05 |  | 2 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 173 | 0.222 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 201857.897 | ng/dscm | 0.00017285 |  | 3 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2010 | 2.893 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 2630076.2804 | ng/dscm | 0.0020093 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 1 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 901 | 1.297 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 1179153.7813 | ng/dscm | 0.00090085 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 2 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2790 | 4.014 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 3649065.9816 | ng/dscm | 0.0027878 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 3 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 145 | 0.1726 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 156921.1118 | ng/dscm | 0.00014466 |  | M26A-1 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 119 | 0.1437 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 130609.2262 | ng/dscm | 0.00011937 |  | M26A-2 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 165 | 0.1936 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 175990.6738 | ng/dscm | 0.00016486 |  | M26A-3 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 144 | 0.1743 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 158471.7465 | ng/dscm | 0.00014442 |  | M26A-1 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 247 | 0.2982 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 271134.5719 | ng/dscm | 0.00024709 |  | M26A-2 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 165 | 0.1986 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 180578.8562 | ng/dscm | 0.00016457 |  | M26A-3 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 34300 | 37.26 | mg/Nm3 | Poor | 2010-05-18 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 33875239.1616 | ng/dscm | 0.034301 |  | M29-1 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 33300 | 36.2 | mg/Nm3 | Poor | 2010-05-19 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 32905123.1855 | ng/dscm | 0.033319 |  | M29-2 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 35800 | 38.88 | mg/Nm3 | Poor | 2010-05-21 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 35349848.2739 | ng/dscm | 0.035794 |  | M29-3 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 23000 | 34.64 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 31487650.351 | ng/dscm | 0.022956 |  | 1 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 58100 | 87.62 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 79652011.1421 | ng/dscm | 0.058071 |  | 2 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 46600 | 70.31 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 63919017.891 | ng/dscm | 0.046601 |  | M5-3 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 21500 | 24.65 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 221236 | dscfm | 6.7 % moisture, 13.5 % CO2, 5.2 % O2, 329 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.021491 |  | 1 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 53300 | 61.3 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 214647 | dscfm | 7.5 % moisture, 13.8 % CO2, 4.9 % O2, 331.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.053314 |  | 2 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 45900 | 52.77 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 211618 | dscfm | 7.5 % moisture, 13.8 % CO2, 5 % O2, 330.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.04588 |  | 3 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 50500 | 57.98 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 243429 | dscfm | 9.67 % moisture, 13.4 % CO2, 5.24 % O2, 312.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050479 |  | 1 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 39700 | 45.66 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 238673 | dscfm | 9.3 % moisture, 13.5 % CO2, 5.17 % O2, 318.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.039739 |  | 2 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 57500 | 66.04 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 252861 | dscfm | 9.46 % moisture, 13.5 % CO2, 5.17 % O2, 318.4 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.057522 |  | 3 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 50900 | 76.79 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 69812159.5852 | ng/dscm | 0.050897 |  | 1 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 40100 | 60.57 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 55060878.2362 | ng/dscm | 0.040142 |  | 2 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 58600 | 88.41 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 80375190.6046 | ng/dscm | 0.058598 |  | M5-3 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 48900 | 73.77 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 67061303.5077 | ng/dscm | 0.048891 |  | 1 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 49500 | 74.75 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 67953498.3107 | ng/dscm | 0.049542 |  | 2 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 50700 | 76.47 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 69518965.3244 | ng/dscm | 0.050683 |  | M5-3 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 49100 | 56.4 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 223578 | dscfm | 9.2 % moisture, 13.1 % CO2, 5.44 % O2, 310.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.049067 |  | 1 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 50300 | 57.82 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 231515 | dscfm | 9.3 % moisture, 13 % CO2, 5.59 % O2, 313.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050302 |  | 2 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 50600 | 58.14 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 223095 | dscfm | 9.7 % moisture, 13 % CO2, 5.5 % O2, 316.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050585 |  | 3 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 76 | 0.105 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 95497.0683 | ng/dscm | 7.6046e-05 |  | 1 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 30.8 | 0.04254 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 38672.6418 | ng/dscm | 3.0756e-05 | above detection level | 2 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 20.4 | 0.02805 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 25499.9639 | ng/dscm | 2.0397e-05 | above detection limit | 3 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 88.4 | 0.1244 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 113101.2757 | ng/dscm | 8.8371e-05 |  | 1 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 36.1 | 0.05191 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 47193.6198 | ng/dscm | 3.6062e-05 |  | 2 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 43.6 | 0.06345 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 57679.1838 | ng/dscm | 4.3594e-05 |  | 3 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 2 |  | 270 | 0.3356 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 305046.6296 | ng/dscm | 0.00026965 | Blank = | 2 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 3 |  | 159 | 0.2029 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 184469.1855 | ng/dscm | 0.00015929 | Blank = | 3 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 4 |  | 247 | 0.3252 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 295628.5104 | ng/dscm | 0.00024718 | Blank = | 4 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 1 |  | 200 | 0.2696 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 245122.2647 | ng/dscm | 0.00019951 | Blank = | 1 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 2 |  | 185 | 0.2504 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 227591.5684 | ng/dscm | 0.00018507 | Blank = | 2 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 3 |  | 175 | 0.2409 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 219016.8995 | ng/dscm | 0.00017452 | Blank = | 3 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 241 | 0.2952 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 268359.438 | ng/dscm | 0.00024078 | Blank = | 1 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 203 | 0.2431 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221030.9063 | ng/dscm | 0.00020283 | Blank = | 2 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 473 | 0.5631 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 511941.4703 | ng/dscm | 0.0004726 | Blank = | 3 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 319 | 0.4245 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 385940.0936 | ng/dscm | 0.00031908 | Blank = | 1 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 194 | 0.2625 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 238606.2222 | ng/dscm | 0.00019412 | Blank = | 2 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 197 | 0.2589 | mg/Nm3 | Unknown | 2010-03-24 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 235406.4554 | ng/dscm | 0.00019732 | Blank = | 3 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 | < | 80.2 | 0.1123 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 102091.8531 | ng/dscm | 8.0156e-05 | [ | 3 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 | < | 81.3 | 0.1134 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 103052.2101 | ng/dscm | 8.131e-05 | [ | 1 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 | < | 79.4 | 0.1105 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 100450.606 | ng/dscm | 7.9356e-05 | [ | 2 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 | < | 87.4 | 0.1167 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 106086.3318 | ng/dscm | 8.7379e-05 | [ | R3 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 | < | 83.6 | 0.112 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 101842.9776 | ng/dscm | 8.3614e-05 | [ | R1 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 | < | 84.7 | 0.1135 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 103195.2825 | ng/dscm | 8.4724e-05 | [ | R2 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 3 | UNK | 33000 | 45.48 | mg/Nm3 | Poor | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 41343394.5646 | ng/dscm | 0.032967 |  | M29-3 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 1 | UNK | 19600 | 17.98 | mg/Nm3 | Poor | 2010-05-11 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 16349504.3298 | ng/dscm | 0.0196 |  | M29-1 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 2 | UNK | 18500 | 17.13 | mg/Nm3 | Poor | 2010-05-12 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 15575454.529 | ng/dscm | 0.0185 |  | M29-2 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 355 | 0.4513 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 410247.309 | ng/dscm | 0.00035512 |  | 1 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 426 | 0.5336 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 485130.1275 | ng/dscm | 0.00042636 |  | 3 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 338 | 0.4266 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 387823.4487 | ng/dscm | 0.00033773 |  | 2 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 300 | 0.4061 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 369225.9224 | ng/dscm | 0.00030005 |  | 1 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 395 | 0.511 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 464527.7403 | ng/dscm | 0.00039511 |  | 2 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 318 | 0.4083 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 371149.696 | ng/dscm | 0.00031781 |  | 3 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1310 | 1.619 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1471728.094 | ng/dscm | 0.0013131 |  | 1 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1980 | 2.384 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 2167219.2907 | ng/dscm | 0.001975 |  | 2 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1270 | 1.593 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1448276.5761 | ng/dscm | 0.0012656 |  | 3 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 3 |  | 9420 | 12.66 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 11504614.4405 | ng/dscm | 0.0094151 |  | 3 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 1 |  | 5100 | 6.849 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 6225957.2026 | ng/dscm | 0.0051017 |  | 1 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 2 |  | 696 | 0.9339 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 849038.4615 | ng/dscm | 0.00069573 |  | 2 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 1 |  | 433 | 0.5916 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 537799.7716 | ng/dscm | 0.00043345 |  | 1 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 2 |  | 235 | 0.3068 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 278905.2259 | ng/dscm | 0.00023488 |  | 2 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 3 |  | 276 | 0.3583 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 325727.592 | ng/dscm | 0.00027595 |  | 3 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 14600 | 16.45 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14956557.2307 | ng/dscm | 0.014567 | 66400 | 1 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 16000 | 18.25 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 16592782.4044 | ng/dscm | 0.016001 | 72600 | 2 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 10400 | 11.53 | mg/Nm3 | Unknown | 2010-05-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 10478398.8886 | ng/dscm | 0.010355 | 45700 | 3 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 80.2 | 0.09791 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 89008.1802 | ng/dscm | 8.0187e-05 | Analytical result between the MDL and the LOQ, value should be considered an estimate. Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does no | 1 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 50 | 0.06128 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 55708.8814 | ng/dscm | 4.9977e-05 | Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does not meet the criteria of 40 CFR Part 136 B, MDL = 1/10 the concentration of the standard u | 2 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 56.1 | 0.06949 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 63168.5838 | ng/dscm | 5.6119e-05 | Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does not meet the criteria of 40 CFR Part 136 B, MDL = 1/10 the concentration of the standard u | 3 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 36700 | 49.15 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 44684957.6536 | ng/dscm | 0.036665 |  | 1 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27600 | 36.22 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 32926912.745 | ng/dscm | 0.027628 |  | 2 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 31800 | 40.99 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 37263211.3771 | ng/dscm | 0.031787 |  | 3 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 36700 | 46.56 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 26A-Mod | 273787 | dscfm | 7.4 % moisture, 14.62 % CO2, 5.15 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 29.47 | ppmv | 0.0367 |  | 1 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27600 | 34.3 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 26A-Mod | 280046 | dscfm | 7.32 % moisture, 14.83 % CO2, 5.01 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 21.71 | ppmv | 0.0276 |  | 2 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 31800 | 38.82 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 26A-Mod | 277907 | dscfm | 7.19 % moisture, 14.77 % CO2, 5.06 % O2, 316 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 24.57 | ppmv | 0.0318 |  | 3 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 1 |  | 305 | 0.3714 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 337641.9869 | ng/dscm | 0.00030527 | ADL Sample 1 1794, BDL Sample 2 [<260] | 1 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 2 |  | 296 | 0.3647 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 331568.6924 | ng/dscm | 0.00029589 | ADL Sample 1 731, ADL Sample 2 [<170] | 2 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 3 |  | 263 | 0.3253 | mg/Nm3 | Poor | 2010-03-11 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 295772.289 | ng/dscm | 0.00026289 | ADL Sample 1 755, BDL Sample 2 [<65] | 3 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 1 |  | 421 | 0.5277 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 479687.9773 | ng/dscm | 0.0004206 | ADL Sample 1 977, ADL Sample 2 527 BDL Sample 3 [<150] | 1 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 2 |  | 279 | 0.3523 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 320246.7012 | ng/dscm | 0.00027912 | ADL Sample 1 817, BDL Sample 2 [<120] | 2 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 3 |  | 298 | 0.3757 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 341564.385 | ng/dscm | 0.00029827 | ADL Sample 1 768, BDL Sample 2 [<240] | 3 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 1 |  | 33400 | 34.56 | mg/Nm3 | Unknown | 2010-06-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 31422725.1037 | ng/dscm | 0.033409 |  | M29-1 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 2 |  | 39000 | 39.65 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 36043156.7913 | ng/dscm | 0.038971 |  | M29-2 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 3 |  | 34900 | 35.25 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 32043470.7871 | ng/dscm | 0.034942 |  | M29-3 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 1 | UNK | 155 | 0.1899 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 172600.0621 | ng/dscm | 0.00015508 |  | M26A-1 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 2 | UNK | 146 | 0.1785 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 162303.5344 | ng/dscm | 0.00014583 |  | M26A-2 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 3 | UNK | 189 | 0.2376 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 215978.7389 | ng/dscm | 0.00018874 |  | M26A-3 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 1 |  | 340 | 0.3694 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 335802.643 | ng/dscm | 0.0003403 |  | 1 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 2 |  | 229 | 0.2479 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 225408.5024 | ng/dscm | 0.00022915 |  | 2 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 3 |  | 162 | 0.173 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 157242.9181 | ng/dscm | 0.00016179 |  | 3 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 59 | 0.08133 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 73936.8677 | ng/dscm | 5.9031e-05 |  | 1 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 71 | 0.09783 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 88935.9398 | ng/dscm | 7.0962e-05 |  | 2 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 76.8 | 0.1063 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 96645.7278 | ng/dscm | 7.6826e-05 |  | 3 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 247 | 0.328 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 298139.4268 | ng/dscm | 0.00024684 |  | 1 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 155 | 0.2005 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 182274.6755 | ng/dscm | 0.00015452 |  | 2 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 286 | 0.3698 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 336166.3375 | ng/dscm | 0.00028555 |  | 3 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 50500 | 62.91 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 57194260.2354 | ng/dscm | 0.050472 | 241147, Blank H20 [<85.2] | M29-1 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 87400 | 109.4 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 99429728.8974 | ng/dscm | 0.087372 | 416811, Blank H20 [<85.2] | M29-2 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 85200 | 106.3 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 96609075.1901 | ng/dscm | 0.085213 | 409396, Blank H20 [<85.2] | M29-3 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 217 | 0.2701 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 245569.1969 | ng/dscm | 0.00021708 | 790, Blank H2O [<78.8] | M26A-1 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 440 | 0.5474 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 497622.2891 | ng/dscm | 0.00044029 | 1602, Blank H2O [<78.8] | M26A-2 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 164 | 0.2054 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 186706.2167 | ng/dscm | 0.00016416 | 597, Blank H20 [<78.8] | M26A-3 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 1 |  | 308 | 0.4078 | mg/Nm3 | Unknown | 2010-06-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 370701.1281 | ng/dscm | 0.00030772 | 882 | 1 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 2 |  | 310 | 0.4133 | mg/Nm3 | Unknown | 2010-06-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 375764.4704 | ng/dscm | 0.00031042 | 1010 | 2 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 3 |  | 386 | 0.4978 | mg/Nm3 | Unknown | 2010-06-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 452584.6442 | ng/dscm | 0.00038598 | 1230 | 3 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 142000 | 153.4 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 139499768.3409 | ng/dscm | 0.14238 |  | M29-1 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 148000 | 160 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 145426264.3823 | ng/dscm | 0.14843 |  | M29-2 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 141000 | 153.3 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 139395789.7402 | ng/dscm | 0.14115 |  | M29-3 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 142000 | 164.3 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26 | 202947 | dscfm | 8.4 % moisture, 10.205475 % CO2, 8.2482563019 % O2, 279.221775 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 93.56 | ppmv | 0.1424 | [5000] | 1 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 149000 | 170.6 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26 | 201486 | dscfm | 8.4 % moisture, 10.185575 % CO2, 8.2729263637 % O2, 298.894075 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 97.53 | ppmv | 0.1485 | [5000] | 2 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 141000 | 164.3 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | EPA method 26 | 203278 | dscfm | 8.4 % moisture, 10.2312 % CO2, 8.2163649782 % O2, 287.949375 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 93.49 | ppmv | 0.1412 | [5000] | 3 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 1 | < | 65 | 0.07899 | mg/Nm3 | Poor | 2010-06-30 | Unknown | Unknown | 399610 | dscfm | 15.1 % moisture, 12 % CO2, 6.8 % O2, 129.3 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.05] | ppmv | [<0.000065] |  | 1 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 136 | 0.158 | mg/Nm3 | Unknown | 2010-07-01 | Unknown | Unknown | 391001 | dscfm | 15.4 % moisture, 11.7 % CO2, 7 % O2, 130.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DDL | DLL | 0.1 | ppmv | 0.000136 |  | 2 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 100 | 0.1264 | mg/Nm3 | Unknown | 2010-07-01 | Unknown | Unknown | 384158 | dscfm | 14.9 % moisture, 11.2 % CO2, 7.6 % O2, 128.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DDL | DLL | 0.08 | ppmv | 0.0001 |  | 3 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 1 | < | 180 | 0.2216 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 201484.3256 | ng/dscm | 0.00017976 | [0.2291] | 1 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 2 |  | 540 | 0.6708 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 609837.5098 | ng/dscm | 0.00054032 |  | 2 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 3 |  | 784 | 0.9668 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 878873.3322 | ng/dscm | 0.00078413 |  | 3 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 677 | 0.8184 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 744008.2387 | ng/dscm | 0.00067726 | ADL | 1 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 947 | 1.145 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1040619.6454 | ng/dscm | 0.00094711 | ADL | 2 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1120 | 1.359 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1235694.7382 | ng/dscm | 0.001116 | ADL | 3 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 811 | 0.9583 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 871162.0321 | ng/dscm | 0.00081137 | ADL | 1 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 999 | 1.191 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1082916.0148 | ng/dscm | 0.00099895 | ADL | 2 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1090 | 1.3 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1182218.0015 | ng/dscm | 0.0010905 | ADL | 3 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 522 | 0.553 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 502748.7744 | ng/dscm | 0.00052234 |  | 1 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 585 | 0.619 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 562718.2641 | ng/dscm | 0.00058512 |  | 2 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 478 | 0.5052 | mg/Nm3 | Unknown | 2010-07-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 459235.542 | ng/dscm | 0.00047791 |  | 3 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 53500 | 55.36 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 50327764.8906 | ng/dscm | 0.053509 |  | U1-M29-1 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 38500 | 41.13 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 37393326.9944 | ng/dscm | 0.038474 |  | U1-M29-3 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 53200 | 53.68 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 48799177.8423 | ng/dscm | 0.053214 |  | U1-M29-2 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 5 |  | 63800 | 61.62 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 56016430.4499 | ng/dscm | 0.063811 |  | U3-26A-5 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 6 |  | 63400 | 62.33 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 56668005.4536 | ng/dscm | 0.063421 |  | U3-26A-6 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 4 |  | 63900 | 61.12 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 55559372.9114 | ng/dscm | 0.063861 |  | U3-26A-4 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 579 | 0.6341 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 576440.3407 | ng/dscm | 0.00057909 |  | 1 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 803 | 0.8728 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 793416.7698 | ng/dscm | 0.0008034 |  | 2 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 444 | 0.4781 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 434652.178 | ng/dscm | 0.00044364 |  | 3 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 88.6 | 0.1238 | mg/Nm3 | Unknown | 2010-11-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 112555.768 | ng/dscm | 8.8645e-05 | See report for detection limit explanation. | M29-1 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 84 | 0.1196 | mg/Nm3 | Unknown | 2010-11-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 108696.8094 | ng/dscm | 8.4049e-05 | See report for detection limit explanation. | M29-2 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 56.5 | 0.07941 | mg/Nm3 | Unknown | 2010-11-09 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 72194.7869 | ng/dscm | 5.6509e-05 | See report for detection limit explanation. | M29-3 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 186000 | 269 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 244544575.3473 | ng/dscm | 0.18568 |  | M29-1 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 178000 | 250.1 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 227326897.1245 | ng/dscm | 0.17772 |  | M29-2 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 170000 | 241.5 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 219552230.9435 | ng/dscm | 0.17013 |  | M29-3 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1010 | 1.331 | mg/Nm3 | Unknown | 2010-03-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1210001.8376 | ng/dscm | 0.0010097 | 935, 370 ug | M29- R1 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1180 | 1.562 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1420276.1114 | ng/dscm | 0.0011767 | 1160, 375 ug | M29-R2 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 991 | 1.326 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1205439.1138 | ng/dscm | 0.00099095 | 1040, 291 ug | M29-R3 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1010 | 1.331 | mg/Nm3 | Unknown | 2010-03-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1210001.8376 | ng/dscm | 0.0010097 | 935, 370 ug | M29- R1 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1180 | 1.562 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1420276.1114 | ng/dscm | 0.0011767 | 1160, 375 ug | M29-R2 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 991 | 1.326 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1205439.1138 | ng/dscm | 0.00099095 | 1040, 291 ug | M29-R3 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2030 | 2.169 | mg/Nm3 | Unknown | 2010-02-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1972136.1319 | ng/dscm | 0.0020275 | 4940 | 1 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1310 | 1.386 | mg/Nm3 | Unknown | 2010-02-24 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 1259996.2957 | ng/dscm | 0.001307 | 3880, [<550] | 2 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1340 | 1.421 | mg/Nm3 | Unknown | 2010-02-25 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 1292003.4932 | ng/dscm | 0.0013402 | 3910. [<530] | 3 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 125 | 0.1479 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 134443.8016 | ng/dscm | 0.0001252 |  | M26A-1 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 |  | 188 | 0.2207 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 200667.2008 | ng/dscm | 0.00018825 |  | M26A-2 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 |  | 225 | 0.2526 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 229627.3287 | ng/dscm | 0.00022536 |  | M26A-3 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 626 | 0.7245 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 658605.0328 | ng/dscm | 0.00062567 |  | M26A-1 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 589 | 0.6809 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 619037.516 | ng/dscm | 0.00058896 |  | M26A-2 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 365 | 0.4236 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 385099.0369 | ng/dscm | 0.00036503 |  | M26A-3 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 604 | 0.5768 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 524350.5002 | ng/dscm | 0.00060378 |  | M26A-1 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 829 | 0.816 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 741855.5805 | ng/dscm | 0.0008288 |  | M26A-2 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 657 | 0.6614 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 601267.1344 | ng/dscm | 0.00065735 |  | M26A-3 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 | < | 269 | 0.3421 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 310970.2412 | ng/dscm | 0.00026898 | [ | 1 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 | < | 256 | 0.3265 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 296780.4705 | ng/dscm | 0.00025602 | [ | 2 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 | < | 257 | 0.3269 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 297210.1754 | ng/dscm | 0.00025673 | [ | 3 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27400 | 29.82 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 27108070.3326 | ng/dscm | 0.027449 |  | M29-2 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 26200 | 28.86 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 26238117.8352 | ng/dscm | 0.026153 |  | M29-3 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 19000 | 20.91 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19012438.3331 | ng/dscm | 0.018951 |  | M29-1 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 56.4 | 0.07686 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 69875.2849 | ng/dscm | 5.6424e-05 | [ | M29-1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 111 | 0.1512 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 137461.9931 | ng/dscm | 0.000111 |  | M29-2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 58 | 0.07897 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 71793.2874 | ng/dscm | 5.7973e-05 | [ | M29-3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 50 | 0.07425 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | EPA method 26 | 33509979 | dscfm | 10.9 % moisture, 12.922825 % CO2, 4.4300675899 % O2, 166.89105 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.047 | ppmv | [<.00005] | [250] | 1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 110 | 0.1453 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26 | 33768324 | dscfm | 10.9 % moisture, 12.940675 % CO2, 4.4073062648 % O2, 166.671625 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.092 | ppmv | 0.00011 | [250] | 2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 60 | 0.07425 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26 | 33693766 | dscfm | 10.9 % moisture, 12.902275 % CO2, 4.4562209265 % O2, 167.349325 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.047 | ppmv | [<.00006] | [250] | 3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 132 | 0.1798 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 163477.8733 | ng/dscm | 0.00013201 |  | M29-1 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 123 | 0.1664 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 151244.6988 | ng/dscm | 0.00012291 |  | M29-2 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 136 | 0.1838 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 167112.564 | ng/dscm | 0.0001358 |  | M29-3 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 541963 | dscfm | 11.1 % moisture, 12.91349858 % CO2, 4.4049060321 % O2, 245.3452786 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1096 | ppmv | 0.0002 | [200] | 1 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 541225 | dscfm | 11.1 % moisture, 12.8878421 % CO2, 4.4376784094 % O2, 244.6899624 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1025 | ppmv | 0.0002 | [200] | 2 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 540995 | dscfm | 11.1 % moisture, 12.88162946 % CO2, 4.4456141427 % O2, 244.9691296 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1119 | ppmv | 0.0002 | [200] | 3 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 1 |  | 102 | 0.1073 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 97519.2061 | ng/dscm | 0.00010249 | HCl 308, Blank N/D | 1 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 2 |  | 128 | 0.1417 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 128783.9175 | ng/dscm | 0.00012805 | HCl 446, Blank ND | 2 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 3 | < | 100 | 0.1081 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 98272.9495 | ng/dscm | 0.00010004 | HCl [ | 3 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 | < | 144 | 0.1848 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 167966.5208 | ng/dscm | 0.00014383 |  | 29-1 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 146 | 0.1895 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 172297.6076 | ng/dscm | 0.00014558 |  | 29-2 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 | < | 147 | 0.1864 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 169494.7789 | ng/dscm | 0.00014711 |  | 29-3 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1150 | 1.321 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 1201320.8731 | ng/dscm | 0.0011515 |  | 1 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 372 | 0.4413 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 401195.8979 | ng/dscm | 0.000372 |  | 2 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 281 | 0.3214 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 292214.4622 | ng/dscm | 0.00028116 |  | 3 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 980 | 1.088 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 989202.4132 | ng/dscm | 0.00097987 |  | 1 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 634 | 0.7371 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 670047.0431 | ng/dscm | 0.00063371 |  | 2 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 357 | 0.4246 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 385985.6184 | ng/dscm | 0.00035685 |  | 3 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 660 | 0.7658 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 696146.2655 | ng/dscm | 0.00066035 |  | 1 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 635 | 0.7375 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 670461.6853 | ng/dscm | 0.00063458 |  | 2 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 567 | 0.6627 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 602428.0124 | ng/dscm | 0.00056682 |  | 3 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 132 | 0.1851 | mg/Nm3 | Unknown | 2010-05-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 168270.6051 | ng/dscm | 0.00013241 |  | 1 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 134 | 0.1882 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 171064.3574 | ng/dscm | 0.00013436 |  | 2 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 127 | 0.1795 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 163217.8375 | ng/dscm | 0.00012711 |  | 3 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | < | 68.1 | 0.08929 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81170.2361 | ng/dscm | 6.8132e-05 | ND, MDL Listed | 1 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | < | 73.4 | 0.09624 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 87492.8848 | ng/dscm | 7.3439e-05 | ND, MDL Listed | 2 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 74.8 | 0.09023 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 82028.1997 | ng/dscm | 7.4754e-05 | ND, MDL listed | 3 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 196 | 0.2454 | mg/Nm3 | Unknown | 2010-02-17 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 223079.3596 | ng/dscm | 0.00019638 | Blank = 0.0385 | 1 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 255 | 0.3287 | mg/Nm3 | Unknown | 2010-02-18 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 298833.3559 | ng/dscm | 0.00025455 | Blank = 0.0385 | 2 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 203 | 0.2637 | mg/Nm3 | Unknown | 2010-02-19 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 239739.6672 | ng/dscm | 0.00020258 | Blank = 0.0385 | 3 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 102 | 0.1465 | mg/Nm3 | Unknown | 2010-02-23 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 133167.591 | ng/dscm | 0.00010196 | 0.0385 (BLANK) | 1 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 167 | 0.2344 | mg/Nm3 | Unknown | 2010-02-25 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 213094.9191 | ng/dscm | 0.00016711 | 0.0385 (Blank) | 3 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 159 | 0.2228 | mg/Nm3 | Unknown | 2010-02-24 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 202574.3992 | ng/dscm | 0.00015861 | 0.0385 (Blank) | 2 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 56.7 | 0.0748 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 0 | ng/dscm | 5.67e-05 | G - Elevated reporting Limit due to matrix interference | 1 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 131 | 0.1724 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | B, G | DLL | 156690.9256 | ng/dscm | 0.00013126 | B - estimated result, less than reporting limit G- elevated reporting limit due to matrix interference | 2 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 177 | 0.2293 | mg/Nm3 | Unknown | 2010-05-27 | Not Specified | EPA method 26A | [5 empty] | B, G | DLL | 208453.606 | ng/dscm | 0.00017683 | B - Estimated results is less than reporting limit G- elevated reporting limit due to matrix interference | 3 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 1 |  | 138 | 0.1278 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 116180.7572 | ng/dscm | 0.00013842 |  | 1 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 2 |  | 134 | 0.1218 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 110699.382 | ng/dscm | 0.00013384 |  | 2 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 3 |  | 484 | 0.4407 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 400596.9436 | ng/dscm | 0.00048364 |  | 3 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 1 |  | 236 | 0.2724 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 247643.8014 | ng/dscm | 0.00023567 |  | 1 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 2 |  | 282 | 0.3251 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 295574.5406 | ng/dscm | 0.00028242 |  | 2 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 3 |  | 397 | 0.4575 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 415927.2751 | ng/dscm | 0.00039738 |  | 3 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 1 | < | 312 | 0.3722 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 338361.9386 | ng/dscm | 0.00031156 | [ | M26A-1 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 2 | < | 379 | 0.4532 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 412009.5423 | ng/dscm | 0.00037924 | [ | M26A-2 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 3 | < | 527 | 0.6338 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 576212.0826 | ng/dscm | 0.00052745 | [ | M26A-3 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 679 | 0.816 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 741853.1626 | ng/dscm | 0.00067883 | [ | M23-2 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 695 | 0.8297 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 754257.6477 | ng/dscm | 0.00069515 | [ | M23-3 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 691 | 0.8306 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 755047.7249 | ng/dscm | 0.0006909 | [ | M23-1 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 | < | 68.8 | 0.09093 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 82666.1832 | ng/dscm | 6.8755e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 1 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 | < | 81.7 | 0.1058 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 96215.7054 | ng/dscm | 8.1674e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 2 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 | < | 69.7 | 0.08974 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81584.3127 | ng/dscm | 6.9671e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 3 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 35.9 | 0.04579 | mg/Nm3 | Unknown | 2010-06-05 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 41626.957 | ng/dscm | 3.5885e-05 |  | 1 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 36.5 | 0.04568 | mg/Nm3 | Unknown | 2010-06-05 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 41525.5831 | ng/dscm | 3.6538e-05 |  | 2 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 34.9 | 0.0442 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 40183.5924 | ng/dscm | 3.4876e-05 |  | 3 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 66.7 | 0.08631 | mg/Nm3 | Unknown | 2010-05-10 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 78464.9484 | ng/dscm | 6.674e-05 |  | 1 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 95.9 | 0.1232 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 111967.0312 | ng/dscm | 9.5874e-05 |  | 2 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 66.1 | 0.0889 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 80817.4366 | ng/dscm | 6.6097e-05 |  | 3 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 |  | 29200 | 39.13 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 35576759.4031 | ng/dscm | 0.029171 |  | 1 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 |  | 36300 | 48.39 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 43988026.0187 | ng/dscm | 0.036278 |  | 2 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 |  | 53700 | 71.16 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 64689627.9183 | ng/dscm | 0.053733 |  | 3 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 |  | 35400 | 45.36 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 41237110.1708 | ng/dscm | 0.035429 |  | 1 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 |  | 46800 | 60.62 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 55106156.1138 | ng/dscm | 0.046778 |  | 2 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 |  | 41200 | 54.93 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 49935324.6266 | ng/dscm | 0.04121 |  | 3 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 1100 | 1.332 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 140180 | dscfm | 17.07 % moisture, 12.6 % CO2, 7.1 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.8434 | ppmv | 0.0011 | [200] | 2 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 800 | 0.9624 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 143391 | dscfm | 15.65 % moisture, 12.7 % CO2, 7 % O2, 321 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.60919 | ppmv | 0.0008 | [200] | 3 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 600 | 0.7262 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 148759 | dscfm | 14.1 % moisture, 12.7 % CO2, 7.1 % O2, 312 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.45963 | ppmv | 0.0006 | [200] | 1 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 71300 | 93.45 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 84956472.6671 | ng/dscm | 0.07131 |  | M26A-1 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 71800 | 95.27 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 86610297.2563 | ng/dscm | 0.071754 |  | M26A-2 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 84500 | 112.2 | mg/Nm3 | Poor | 2010-05-26 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 101960289.0366 | ng/dscm | 0.084471 |  | M26A-3 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 149 | 0.1916 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 174192.6575 | ng/dscm | 0.00014916 |  | M26A-1 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 186 | 0.2385 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 216775.0621 | ng/dscm | 0.00018562 |  | M26A-2 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 213 | 0.2724 | mg/Nm3 | Unknown | 2010-07-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 247597.7963 | ng/dscm | 0.00021344 |  | M26A-3 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 327 | 0.3835 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 348647.248 | ng/dscm | 0.00032707 |  | M26A-1 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 254 | 0.3006 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 273266.6096 | ng/dscm | 0.00025449 |  | M26A-2 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 356 | 0.4301 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 390967.4563 | ng/dscm | 0.0003563 |  | M26A-3 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 480 | 0.7428 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.7531 | ng/dscm | 0.0004802 |  | M5/29-1 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 540 | 0.8148 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 740714.8499 | ng/dscm | 0.00053951 |  | M5/29-2 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 604 | 0.9497 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 863405.492 | ng/dscm | 0.00060418 |  | M5/29-3 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 602 | 0.7787 | mg/Nm3 | Unknown | 2010-07-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 707865.2315 | ng/dscm | 0.00060188 |  | M5/29-1 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 684 | 0.8964 | mg/Nm3 | Unknown | 2010-07-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 814924.0293 | ng/dscm | 0.00068428 |  | M5/29-2 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 637 | 0.8361 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 760078.051 | ng/dscm | 0.00063738 |  | M5/29-3 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 665 | 0.8924 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 811266.5033 | ng/dscm | 0.0006649 | Lab J flag result between MDL and LOQ | 1 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 819 | 1.099 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 999260.3795 | ng/dscm | 0.00081861 | Lab J flag result between MDL and LOQ | 2 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 710 | 0.9462 | mg/Nm3 | Unknown | 2010-05-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 860211.3717 | ng/dscm | 0.00070962 | Lab J flag result between MDL and LOQ | 3 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 16.1 | 0.01684 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 15305.017 | ng/dscm | 1.61e-05 |  | 1 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 14.6 | 0.02018 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 18349.9584 | ng/dscm | 1.4563e-05 |  | 2 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 14.1 | 0.01966 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 17869.0681 | ng/dscm | 1.4098e-05 |  | 3 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 206 | 0.2436 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221418.4774 | ng/dscm | 0.00020554 | 0.04 | 1 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 149 | 0.1763 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 160279.7501 | ng/dscm | 0.00014879 | 0.03 | 2 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 219 | 0.2592 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 235680.3502 | ng/dscm | 0.00021878 | 0.02 | 3 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 1 |  | 23900 | 30.78 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 27984307.6923 | ng/dscm | 0.02394 |  | 1 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 2 |  | 18300 | 23.95 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21775222.861 | ng/dscm | 0.018318 |  | 2 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 3 |  | 20100 | 26.77 | mg/Nm3 | Unknown | 2010-06-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 24335792.0131 | ng/dscm | 0.020137 |  | 3 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 283 | 0.3187 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 289731.2884 | ng/dscm | 0.00028283 | [ | 1 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 286 | 0.3221 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 292853.8115 | ng/dscm | 0.00028609 | [ | 2 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 289 | 0.3242 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 294712.8878 | ng/dscm | 0.00028879 | [ | 3 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 283 | 0.3187 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 289731.2884 | ng/dscm | 0.00028283 | [ | 1 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 286 | 0.3221 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 292853.8115 | ng/dscm | 0.00028609 | [ | 2 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 289 | 0.3242 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 294712.8878 | ng/dscm | 0.00028879 | [ | 3 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 274 | 0.3026 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 275058.9798 | ng/dscm | 0.00027374 | [ | 1 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 311 | 0.3461 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 314676.2426 | ng/dscm | 0.00031147 | 392 ug | 2 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 394 | 0.438 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 398214.8729 | ng/dscm | 0.00039385 | 480 ug | 3 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 291 | 0.323 | mg/Nm3 | Unknown | 2010-08-24 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 293627.2298 | ng/dscm | 0.00029108 | [ | 1 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 276 | 0.3076 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 279632.0876 | ng/dscm | 0.00027635 | [ | 2 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 283 | 0.3161 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 287334.6814 | ng/dscm | 0.00028287 | [ | 3 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 434 | 0.5989 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 544429.7426 | ng/dscm | 0.0004344 |  | M26A-1 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 518 | 0.7201 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 654625.8382 | ng/dscm | 0.00051844 |  | M26A-2 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 505 | 0.6851 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 622787.6557 | ng/dscm | 0.00050482 |  | M26A-3 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 1 |  | 498 | 0.6441 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 585582.7427 | ng/dscm | 0.00049837 | See laboratory report for additional information. | 1 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 759 | 0.9737 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 885188.1404 | ng/dscm | 0.00075851 | See laboratory report for additional information. | 2 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 990 | 1.279 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1162890.9435 | ng/dscm | 0.00098969 | See laboratory report for additional information. | 3 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 7600 | 10.89 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9898238.141 | ng/dscm | 0.0075985 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-1 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 7280 | 10.54 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9583149.111 | ng/dscm | 0.0072778 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-2 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 6950 | 10.06 | mg/Nm3 | Unknown | 2010-04-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9149592.2743 | ng/dscm | 0.0069485 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-3 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 7630 | 10.36 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 163426 | dscfm | 7.47 % moisture, 14.7 % CO2, 4.36 % O2, 414 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.56 | ppmv | 0.00763 | 26A | 1 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 7310 | 10.1 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 163351 | dscfm | 7.13 % moisture, 14.81 % CO2, 3.97 % O2, 417 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.39 | ppmv | 0.00731 | 26A | 2 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 6960 | 9.558 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 160792 | dscfm | 7.49 % moisture, 14.77 % CO2, 4.09 % O2, 417 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.05 | ppmv | 0.00696 | 26A | 3 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 261 | 0.3304 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 300351.4872 | ng/dscm | 0.00026068 |  | M26A-1 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 200 | 0.2537 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 230613.7512 | ng/dscm | 0.00020016 |  | M26A-2 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 181 | 0.2298 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 208896.3932 | ng/dscm | 0.00018131 |  | M26A-3 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 1 |  | 344 | 0.4175 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 379535.0232 | ng/dscm | 0.00034367 |  | 1 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 2 |  | 571 | 0.6893 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 626658.448 | ng/dscm | 0.00057109 |  | 2 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 3 |  | 345 | 0.4215 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 383188.8141 | ng/dscm | 0.00034526 |  | 3 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 1 |  | 294 | 0.3617 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 328774.1669 | ng/dscm | 0.00029374 |  | 1 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 2 |  | 454 | 0.5617 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 510655.6766 | ng/dscm | 0.00045402 |  | 2 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 3 |  | 107 | 0.1351 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 122794.3455 | ng/dscm | 0.00010687 |  | 3 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 48.5 | 0.06235 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 56685.6849 | ng/dscm | 4.8538e-05 | [ | M26A-1 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 49.2 | 0.06488 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 58982.6659 | ng/dscm | 4.9185e-05 | [ | M26A-2 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 |  | 96.7 | 0.1267 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 115210.5184 | ng/dscm | 9.6705e-05 |  | M26A-3 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 50 | 0.06084 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1806327 | dscfm | 15.6 % moisture, 12.8 % CO2, 5.9 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 56.7 | ppmv | 5e-05 | [200] | 1 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 50 | 0.06331 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1845061 | dscfm | 16.6 % moisture, 13.1 % CO2, 5.7 % O2, 116 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 59 | ppmv | 5e-05 | [200] | 2 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 |  | 100 | 0.1236 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1845641 | dscfm | 16.5 % moisture, 13.1 % CO2, 5.6 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. Emission factor conversion error | ADL | ADL | 115.2 | ppmv | 5e-05 | [200] | 3 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 100 | 0.1298 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1844595 | dscfm | 15.7 % moisture, 13.4 % CO2, 6 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 121 | ppmv | 0.0001 | [200] | 1 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 50 | 0.06642 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1836298 | dscfm | 16.2 % moisture, 13.3 % CO2, 6 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<61.9] | ppmv | [<0.00005] | [200] | 2 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 50 | 0.06792 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1846014 | dscfm | 16.1 % moisture, 13.3 % CO2, 5.9 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<63.3] | ppmv | [<0.00005] | [200] | 3 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 104 | 0.1331 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 120969.2611 | ng/dscm | 0.00010358 |  | M26A-1 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 52.6 | 0.06806 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 61873.7299 | ng/dscm | 5.2628e-05 | [ | M26A-2 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 52.7 | 0.06821 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 62005.7055 | ng/dscm | 5.274e-05 | [ | M26A-3 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 106 | 0.1262 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [6 empty] | ADL | 114746.7309 | ng/dscm | 0.00010609 |  | M26A-1 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 118 | 0.1491 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [6 empty] | ADL | 135501.6796 | ng/dscm | 0.00011841 |  | M26A-2 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 57 | 0.07173 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 65212.3741 | ng/dscm | 5.6987e-05 | [ | M26A-3 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 110 | 0.1232 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1844402 | dscfm | 15.5 % moisture, 12.2 % CO2, 7 % O2, 116 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 114.8 | ppmv | 0.00011 | [200] | 1 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 120 | 0.1454 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1848466 | dscfm | 15.6 % moisture, 12.2 % CO2, 7.1 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 135.5 | ppmv | 0.00012 | [200] | 2 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 60 | 0.06856 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1844770 | dscfm | 15.9 % moisture, 13.1 % CO2, 6.4 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<63.9] | ppmv | [<.00006] | [200] | 3 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 525 | 0.6495 | mg/Nm3 | Unknown | 2010-07-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 590420.8155 | ng/dscm | 0.00052522 | 690 (in units of ug) | 1 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 151 | 0.1881 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 171016.3172 | ng/dscm | 0.00015058 | 200 (in units of ug; not detected with a reportable detection limit of 200 ug used as the final result) | 2 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 153 | 0.188 | mg/Nm3 | Unknown | 2010-07-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 170937.6891 | ng/dscm | 0.0001534 | 200 (in units of ug; not detected with a reportable detection limit of 200 ug used as the final result) | 3 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 128 | 0.1768 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 160686.5934 | ng/dscm | 0.00012786 |  | 1 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 167 | 0.231 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 209978.6876 | ng/dscm | 0.00016708 |  | 2 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 148 | 0.204 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 185434.9635 | ng/dscm | 0.00014755 |  | 3 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 128 | 0.1675 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 220060 | dscfm | 18.2 % moisture, 14 % CO2, 4.8 % O2, 183 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.106 | ppmv | 0.000128 |  | 1 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 148 | 0.1927 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 221914 | dscfm | 17.6 % moisture, 15.1 % CO2, 4.8 % O2, 190 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.122 | ppmv | 0.000148 |  | 3 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 167 | 0.2196 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 224094 | dscfm | 18.1 % moisture, 15.1 % CO2, 4.8 % O2, 186 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.139 | ppmv | 0.000167 |  | 2 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 625 | 0.8304 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 754931.2977 | ng/dscm | 0.00062496 |  | M5/29-1 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 388 | 0.5671 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 515584.321 | ng/dscm | 0.00038767 |  | M5/29-2 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 449 | 0.6485 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 589561.4205 | ng/dscm | 0.00044856 |  | M027/028-3 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 29900 | 36.58 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 33254468.4211 | ng/dscm | 0.029871 |  | 1 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 25500 | 31.68 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 28802686.2808 | ng/dscm | 0.025493 |  | 2 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 23600 | 29.39 | mg/Nm3 | Unknown | 2010-03-24 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 26717350.3233 | ng/dscm | 0.023576 |  | 3 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 1 | < | 94.3 | 0.1186 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 107814.722 | ng/dscm | 9.434e-05 | [ | 1 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 184 | 0.2575 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 234133.1103 | ng/dscm | 0.00018364 | First section undetected, second section detected. See report for additional information. | 2 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 3 | < | 82.8 | 0.1161 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 105569.3412 | ng/dscm | 8.28e-05 | [ | 3 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 11700 | 13.57 | mg/Nm3 | Unknown | 2010-07-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12340715.8947 | ng/dscm | 0.011661 |  | 1 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 11700 | 13.44 | mg/Nm3 | Unknown | 2010-07-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12222348.8796 | ng/dscm | 0.01165 |  | 2 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 12100 | 14.08 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12801927.5089 | ng/dscm | 0.012121 |  | 3 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 11700 | 13.57 | mg/Nm3 | Unknown | 2010-07-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12340715.8947 | ng/dscm | 0.011661 |  | 1 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 11700 | 13.44 | mg/Nm3 | Unknown | 2010-07-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12222348.8796 | ng/dscm | 0.01165 |  | 2 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 12100 | 14.08 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12801927.5089 | ng/dscm | 0.012121 |  | 3 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 136 | 0.1901 | mg/Nm3 | Unknown | 2010-06-01 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 172863.5959 | ng/dscm | 0.00013622 |  | 1 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 39200 | 55.97 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 50882374.1266 | ng/dscm | 0.039157 |  | 2 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 41300 | 56.95 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 51769879.0766 | ng/dscm | 0.041348 |  | 3 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 101 | 0.1338 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 121614.0024 | ng/dscm | 0.00010051 | See test report regarding detection limit information | M26A-1 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 80 | 0.1064 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 96739.9396 | ng/dscm | 7.9955e-05 | See test report regarding detection limit information | M26A-2 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 109 | 0.1425 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 129566.2511 | ng/dscm | 0.0001092 | See test report regarding detection limit information | M26A-3 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 97.4 | 0.1271 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 115539.6519 | ng/dscm | 9.7378e-05 | See test report regarding detection limit information | M26A-1 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 104 | 0.1325 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 120419.5552 | ng/dscm | 0.00010423 | See test report regarding detection limit information | M26A-2 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 81.7 | 0.1038 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 94352.469 | ng/dscm | 8.167e-05 | See test report regarding detection limit information | M26A-3 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 | < | 410 | 0.5363 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 487590.0027 | ng/dscm | 0.00041008 | [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 | < | 411 | 0.5395 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 490482.3055 | ng/dscm | 0.00041143 | [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 4 | < | 373 | 0.4967 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 451574.1809 | ng/dscm | 0.00037291 | [ | M26A-4 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 | < | 410 | 0.5363 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 487590.0027 | ng/dscm | 0.00041008 | [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 | < | 411 | 0.5395 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 490482.3055 | ng/dscm | 0.00041143 | [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 4 | < | 373 | 0.4967 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 451574.1809 | ng/dscm | 0.00037291 | [ | M26A-4 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 | < | 309 | 0.3591 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 326465.6484 | ng/dscm | 0.00030853 | [ | M29-3 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 | < | 285 | 0.3362 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 305643.4514 | ng/dscm | 0.00028464 | [ | M26A-4 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 5 | < | 311 | 0.3624 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 329429.0412 | ng/dscm | 0.00031133 | [ | M26A-5 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 | < | 407 | 0.4846 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 440553.2904 | ng/dscm | 0.0004073 | [ | M26A-4 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 5 | < | 327 | 0.3839 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 349016.0764 | ng/dscm | 0.00032742 | [ | M26A-5 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 6 | < | 335 | 0.3927 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 356991.7168 | ng/dscm | 0.0003349 | [ | M26A-6 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 1 |  | 1320 | 1.738 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 320 |  |  | 10.7 % moisture, 13.4 % CO2, 6.21 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00073766 | ppmv | 0.00132 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 1 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 2 |  | 1340 | 1.793 | mg/Nm3 | Unknown | 2010-04-10 | Refer to sample method | U.S. EPA Method 320 |  |  | 11.4 % moisture, 13.6 % CO2, 5.95 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00076113 | ppmv | 0.00134 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 2 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 3 |  | 886 | 1.153 | mg/Nm3 | Unknown | 2010-04-10 | Refer to sample method | U.S. EPA Method 320 |  |  | 11.6 % moisture, 13.7 % CO2, 5.84 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00048954 | ppmv | 0.000886 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 3 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 7090 | 9.111 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 8282978.3076 | ng/dscm | 0.007094 | 30000, Blank ND | 1 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 7540 | 10.2 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9271130.7957 | ng/dscm | 0.0075436 | 33900, Blank ND | 2 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 8990 | 12.24 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 11129503.4382 | ng/dscm | 0.0089886 | 40600, Blank ND | 3 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 503 | 0.6373 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 579329.4881 | ng/dscm | 0.00050266 |  | 2 | 947
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 164 | 0.21 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 190880.7752 | ng/dscm | 0.00016442 |  | 3 | 947
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 415 | 2.039 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 19.2 % moisture, 13.4 % CO2, 5 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1900 | ppmv | 0.00041455 |  | 1 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 444 | 2.146 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.7 % moisture, 13.8 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 2000 | ppmv | 0.00044428 |  | 2 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 241 | 1.18 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.9 % moisture, 14.1 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1100 | ppmv | 0.00024144 |  | 3 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 415 | 2.039 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 19.2 % moisture, 13.4 % CO2, 5 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1900 | ppmv | 0.00041455 |  | 1 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 444 | 2.146 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.7 % moisture, 13.8 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 2000 | ppmv | 0.00044428 |  | 2 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 241 | 1.18 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.9 % moisture, 14.1 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1100 | ppmv | 0.00024144 |  | 3 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 1 |  | 5450 | 5.941 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5401093.6698 | ng/dscm | 0.0054461 |  | M29-1 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 2 |  | 5420 | 5.696 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5178473.7733 | ng/dscm | 0.0054242 |  | M29-2 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 3 |  | 6270 | 7.239 | mg/Nm3 | Unknown | 2010-05-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 6580977.1679 | ng/dscm | 0.0062688 |  | M29-3 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 1 |  | 8020 | 8.769 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7971515.8472 | ng/dscm | 0.0080157 | HF 34800, Blank N/D | 1 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 2 |  | 7680 | 8.784 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7985665.9718 | ng/dscm | 0.0076803 | HF 15900, Blank N/D | 2 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 3 |  | 7620 | 8.228 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7479871.7767 | ng/dscm | 0.007617 | HF 32900, Blank N/D | 3 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 71700 | 86 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78183310.5066 | ng/dscm | 0.071711 | 80900+234 ug | 7A-1 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 72000 | 86.65 | mg/Nm3 | Unknown | 2010-04-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78773739.6212 | ng/dscm | 0.071994 | 81900+ 295 ug | 7A-2 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 73400 | 88.33 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 80295953.134 | ng/dscm | 0.073438 | 82400+258 ug | 7A-3 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 70900 | 87.1 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 79181280.654 | ng/dscm | 0.070943 | 82000+ 275 ug | 7B-1 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 72700 | 88.95 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 80860145.7726 | ng/dscm | 0.072652 | 81400+266 ug | 7B-3 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 70800 | 86.82 | mg/Nm3 | Unknown | 2010-04-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78926282.5842 | ng/dscm | 0.070814 | 80900+281 ug | 7B-2 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 35.7 | 0.04313 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 39209.648 | ng/dscm | 3.5682e-05 |  | M23-1 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 78.3 | 0.09626 | mg/Nm3 | Unknown | 2010-06-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 87504.7291 | ng/dscm | 7.8291e-05 |  | M23-2 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 105 | 0.1299 | mg/Nm3 | Unknown | 2010-06-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 118078.889 | ng/dscm | 0.0001055 |  | M23-3 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 | < | 25 | 0.03012 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 27378.0615 | ng/dscm | 2.4968e-05 |  | M29-1 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 16.9 | 0.02017 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 18334.6557 | ng/dscm | 1.6902e-05 |  | M29-2 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 54.7 | 0.06545 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 59501.6647 | ng/dscm | 5.4655e-05 |  | M29-3 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4980 | 6.509 | mg/Nm3 | Poor | 2010-07-13 | Refer to sample method | U.S. EPA Method 26A-Mod | 1328719 | dscfm | 13.53 % moisture, 14.24 % CO2, 4.92 % O2, 331 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 4.12 | ppmv | 0.00498 | Modified Method 26 - non isokinetic | 1 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1360 | 1.754 | mg/Nm3 | Poor | 2010-07-14 | Refer to sample method | U.S. EPA Method 26A-Mod | 1333580 | dscfm | 14.11 % moisture, 14.09 % CO2, 5.12 % O2, 331 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 1.11 | ppmv | 0.00136 | Modified Method 26 - non isokinetic | 2 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1400 | 1.864 | mg/Nm3 | Poor | 2010-07-15 | Refer to sample method | U.S. EPA Method 26A-Mod | 1359968 | dscfm | 12.55 % moisture, 15.1 % CO2, 4.61 % O2, 326 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 1.18 | ppmv | 0.0014 | Modified Method 26 - non isokinetic | 3 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 1380 | 1.732 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1574646.2493 | ng/dscm | 0.001376 |  | 2 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 2630 | 3.339 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 3035071.3662 | ng/dscm | 0.0026342 |  | 3 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 4 |  | 2110 | 2.509 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 2280652.3834 | ng/dscm | 0.0021085 |  | 4 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 | < | 121 | 0.1519 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 138086.0105 | ng/dscm | 0.00012067 | Analysis for HCl was non-detect with detection limit substituted | 1 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 | < | 120 | 0.151 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 137304.5832 | ng/dscm | 0.00011999 | Analysis for HCl was non-detect with detection limit substituted | 2 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 | < | 93.4 | 0.1176 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 106884.0297 | ng/dscm | 9.3403e-05 | Analysis for HCl was non-detect with detection limit substituted | 3 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 | < | 112 | 0.1419 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 129040.0681 | ng/dscm | 0.000112 | Analysis for HCl was non-detect with detection limit substituted | 1 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 | < | 99.2 | 0.1249 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 113505.1439 | ng/dscm | 9.9189e-05 | Analysis for HCl was non-detect with detection limit substituted | 2 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 | < | 161 | 0.2026 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 184226.7032 | ng/dscm | 0.00016099 | Analysis for HCl was non-detect with detection limit substituted | 3 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 | < | 64.2 | 0.08579 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 77989.0837 | ng/dscm | 6.4195e-05 |  | 1 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 | < | 121 | 0.1604 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 145791.6462 | ng/dscm | 0.00012078 |  | 2 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 | < | 103 | 0.1385 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 125886.9182 | ng/dscm | 0.00010296 |  | 3 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 | < | 117 | 0.1552 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 141085.2713 | ng/dscm | 0.00011689 | Analysis for HCl was non-detect with detection limit substituted | 2 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 | < | 114 | 0.1511 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 137376.7862 | ng/dscm | 0.00011381 | Analysis for HCl was non-detect with detection limit substituted | 3 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 | < | 123 | 0.1609 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 146253.2535 | ng/dscm | 0.00012276 | Analysis for HCl was non-detect with detection limit substituted | 1 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 | < | 100 | 0.1478 | mg/Nm3 | Unknown | 2010-03-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 134359.9522 | ng/dscm | 0.00010048 | Non-Detect, Reported as Laboratory Detection Limit | 1 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 | < | 100 | 0.1468 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 133426.2899 | ng/dscm | 0.00010037 | Non-Detect, Reported as Laboratory Detection Limit; Temperature dipped slightly below 248 degF for approximately 30 minutes, which can cause a low bias in measurement. Samples were collected in combined train with HCN, which is contrary to more recent EPA | 2 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 | < | 76.5 | 0.1125 | mg/Nm3 | Unknown | 2010-03-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 102243.1018 | ng/dscm | 7.6461e-05 | Non-Detect, Reported as Laboratory Detection Limit | 3 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 | < | 30 | 0.0452 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 41094.0785 | ng/dscm | 3.0033e-05 | Non-Detect, Reported as Laboratory Detection Limit; Temperature briefly dipped below 248 degF, which can cause a low bias in measurement. Samples were collected in combined train with HCN, which is contrary to more recent EPA recommendations posted on ICR | 1 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 | < | 29.8 | 0.04493 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 40843.0045 | ng/dscm | 2.985e-05 | Non-Detect, Reported as Laboratory Detection Limit | 2 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 | < | 30.7 | 0.0459 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 41727.2987 | ng/dscm | 3.067e-05 | Non-Detect, Reported as Laboratory Detection Limit | 3 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 101000 | 119.5 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 108668890.2645 | ng/dscm | 0.1012 |  | 1 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 109000 | 129.6 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 117849397.1335 | ng/dscm | 0.10896 |  | 2 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 115000 | 136.7 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 124260459.1164 | ng/dscm | 0.11488 |  | 3 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 | < | 74700 | 100.7 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 91504745.7547 | ng/dscm | 0.074696 |  | 1 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 | < | 74000 | 99 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 90002123.4929 | ng/dscm | 0.074006 |  | 2 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 | < | 81400 | 105.9 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 96251284.8708 | ng/dscm | 0.081444 |  | 3 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 | < | 161 | 0.2091 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 190080.6027 | ng/dscm | 0.00016075 | BDL [<150] | 1 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 157 | 0.2055 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 186814.9744 | ng/dscm | 0.00015732 | ADL 276, ADL 161 | 2 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 124 | 0.1613 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 146617.3797 | ng/dscm | 0.00012419 | ADL 167, BDL [<180] | 3 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 88200 | 91.98 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83622017.2061 | ng/dscm | 0.088164 | Impinger Solution 253000, DI Water 7780, Blank 716 | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 88200 | 93.09 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84629159.4416 | ng/dscm | 0.088159 | Impinger Solution 255000, DI Water 6600, Blank 716 | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 91600 | 94.29 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 85720075.0986 | ng/dscm | 0.091594 | Impinger Solution 256000, DI Water 12300, Blank 716 | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 88200 | 91.98 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83622017.2061 | ng/dscm | 0.088164 | Impinger Solution 253000, DI Water 7780, Blank 716 | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 88200 | 93.09 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84629159.4416 | ng/dscm | 0.088159 | Impinger Solution 255000, DI Water 6600, Blank 716 | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 91600 | 94.29 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 85720075.0986 | ng/dscm | 0.091594 | Impinger Solution 256000, DI Water 12300, Blank 716 | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 1830 | 2.101 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 164477 | dscfm | 10.92 % moisture, 10.5 % CO2, 9.3 % O2, 318 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0018339 |  | 1 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 1570 | 1.801 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | EPA method 26 | 166539 | dscfm | 8.78 % moisture, 10.5 % CO2, 9.5 % O2, 323 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0015704 |  | 2 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 1590 | 1.817 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | EPA method 26 | 168741 | dscfm | 8.73 % moisture, 10.5 % CO2, 9.5 % O2, 324 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0015856 |  | 3 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 1 |  | 15600 | 21.2 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19273147.649 | ng/dscm | 0.015618 |  | M5/29-1 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 2 |  | 15500 | 21.19 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19266275.372 | ng/dscm | 0.015469 |  | M5/29-2 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 3 |  | 17000 | 23.43 | mg/Nm3 | Unknown | 2010-05-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21300162.8283 | ng/dscm | 0.017016 |  | M5/29-3 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 | < | 72.5 | 0.08923 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81121.9236 | ng/dscm | 7.2478e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 1 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 | < | 78 | 0.09566 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 86966.4477 | ng/dscm | 7.7973e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 2 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 | < | 82.4 | 0.1024 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 93119.4488 | ng/dscm | 8.2447e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 3 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 30.6 | 0.0346 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 322 | 834323 | dscfm | 200.5 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.0219 | ppmv | 3.0566e-05 | 0.602,[<0.02],0.021,DLL | Sample 3 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 29.5 | 0.03349 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 321 | 829503 | dscfm | 200.9 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.0212 | ppmv | 2.9482e-05 | 0.602,[<0.02],0.021,DLL | Sample 2 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 858 | 0.9726 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 320 | 829805 | dscfm | 201.2 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.6156 | ppmv | 0.00085788 | 0.602,[<0.02],0.021,DLL | Sample 1 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 6580 | 8.856 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 320 | 834669 | dscfm | 15.6 % moisture, 195.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 4.72 | ppmv | 0.00658 | 4.7734,5.3198,[<0.02],DLL | Sample 1 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 7330 | 9.846 | mg/Nm3 | Unknown | 2010-05-09 | Refer to sample method | U.S. EPA Method 321 | 847024 | dscfm | 15.6 % moisture, 195 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 5.26 | ppmv | 0.00733 | 4.7734,5.3198,[<0.02],DLL | Sample 2 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 28.5 | 0.03828 | mg/Nm3 | Unknown | 2010-05-09 | Refer to sample method | U.S. EPA Method 322 | 832041 | dscfm | 15.8 % moisture, 192.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 0.0205 | ppmv | 2.85e-05 | 4.7734,5.3198,[<0.02],DLL | Sample 3 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 | UNK | 1440 | 1.998 | mg/Nm3 | Poor | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1816008.4463 | ng/dscm | 0.00144 |  | 1 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | UNK | 1500 | 2.047 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1861060.3484 | ng/dscm | 0.0014952 |  | 2 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | UNK | 2390 | 3.428 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 3116094.8239 | ng/dscm | 0.0023878 |  | 3 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 16 | 0.02313 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21031.3207 | ng/dscm | 1.5953e-05 |  | 1 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 18.3 | 0.02608 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 23709.6707 | ng/dscm | 1.8267e-05 |  | 2 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | < | 16.6 | 0.0228 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 20726.4832 | ng/dscm | 1.6579e-05 |  | 3 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 29.9 | 0.04293 | mg/Nm3 | Unknown | 2010-04-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 39028.2878 | ng/dscm | 2.9888e-05 |  | 1 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 9.39 | 0.01361 | mg/Nm3 | Unknown | 2010-04-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 12374.746 | ng/dscm | 9.3866e-06 |  | 2 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | < | 9.08 | 0.01324 | mg/Nm3 | Unknown | 2010-04-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 12038.4809 | ng/dscm | 9.0776e-06 |  | 3 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 | < | 13.6 | 0.0192 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 17454.0423 | ng/dscm | 1.3578e-05 |  | 1 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 13.4 | 0.01962 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 17836.1318 | ng/dscm | 1.3418e-05 |  | 2 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 |  | 88.3 | 0.1107 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 100659.2822 | ng/dscm | 8.8265e-05 |  | 3 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1550 | 1.916 | mg/Nm3 | Unknown | 2010-06-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1741920.5106 | ng/dscm | 0.0015541 |  | 1 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 869 | 1.071 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 973935.8584 | ng/dscm | 0.00086895 |  | 2 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 725 | 0.838 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 761829.6765 | ng/dscm | 0.00072536 |  | 3 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 51000 | 57.03 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 368595 | dscfm | 7.4 % moisture, 10.5 % CO2, 8.2 % O2, 285.3 deg F | The data was corrected by the sample contractor for sample line bias due to known off-gassing of formaldehyde from heated sample lines. One-half the average system zero concentration accounted for 30 to 50% of the uncorrected test run results. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.051 |  | 1 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 52000 | 63.35 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 367737 | dscfm | 7.2 % moisture, 10.4 % CO2, 8.3 % O2, 287.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.052 |  | 2 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 52000 | 63.35 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 368102 | dscfm | 7.3 % moisture, 10.3 % CO2, 8.4 % O2, 288.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.052 |  | 3 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 15500 | 19.69 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 17899885.077 | ng/dscm | 0.015493 |  | 1 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 15700 | 21.15 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19228238.5998 | ng/dscm | 0.015742 |  | 2 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 16800 | 22.36 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 20322891.376 | ng/dscm | 0.016843 |  | 3 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 | UNK | 17900 | 24.65 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 22410958.3928 | ng/dscm | 0.017871 |  | M29-1 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 | UNK | 16700 | 23.18 | mg/Nm3 | Poor | 2010-05-26 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 21073161.1894 | ng/dscm | 0.016699 |  | M29-2 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 3 | UNK | 19000 | 25.59 | mg/Nm3 | Poor | 2010-05-28 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 23261147.4838 | ng/dscm | 0.019024 |  | M29-3 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | < | 65 | 0.08238 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 74888.8964 | ng/dscm | 6.4998e-05 | Sample Below Detection Limit | 1 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | < | 65 | 0.08008 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 72800.1253 | ng/dscm | 6.4952e-05 | Lower Reportable limit from lab 250 ug | 2 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 65.5 | 0.08354 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 75941.9642 | ng/dscm | 6.5467e-05 | Lab reporting limit 250 ug | 3 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 1 |  | 563 | 0.6493 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | EPA method 26 | 245541 | dscfm | 6.8 % O2, 294.3 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.411 | ppmv | 0.000563 |  | 1 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 2 |  | 776 | 0.8942 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | EPA method 26 | 245758 | dscfm | 6.8 % O2, 297.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.566 | ppmv | 0.000776 |  | 2 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 3 |  | 578 | 0.6604 | mg/Nm3 | Unknown | 2010-07-21 | Refer to sample method | EPA method 26 | 246190 | dscfm | 6.9 % O2, 290 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.418 | ppmv | 0.000578 |  | 3 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 214 | 0.2574 | mg/Nm3 | Unknown | 2010-03-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 234016.1319 | ng/dscm | 0.00021416 | 1.39ug/ml, 0.266ug/ml (Blank), 665ml sample volume - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven | 2 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 211 | 0.2569 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 233557.4938 | ng/dscm | 0.00021118 | 1.39ug/ml, 0.266ug/ml (Blank), 690 ml sample vol. - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven | 3 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 4 |  | 208 | 0.2551 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 231913.0116 | ng/dscm | 0.00020798 | 1.34ug/ml, 0.266ug/ml (Blank), 700 ml sample - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven injec | 4 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 923 | 1.121 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1019294.7871 | ng/dscm | 0.00092297 | 2840 ug | 1 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 802 | 0.9759 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 887163.122 | ng/dscm | 0.00080162 | 2440 ug | 2 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 909 | 1.107 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1006644.615 | ng/dscm | 0.00090894 | 2740 ug | 3 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 91000 | 92.69 | mg/Nm3 | Unknown | 2010-02-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84265364.4925 | ng/dscm | 0.090953 | 342 | 1 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 99700 | 98.87 | mg/Nm3 | Unknown | 2010-02-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 89884370.2732 | ng/dscm | 0.09967 | 355 | 2 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 98800 | 93.04 | mg/Nm3 | Unknown | 2010-02-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84585615.395 | ng/dscm | 0.098833 | 338 | 3 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 1 |  | 13400 | 15.76 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14329683.1043 | ng/dscm | 0.013423 |  | 1 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 2 |  | 12700 | 14.95 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 13586692.8606 | ng/dscm | 0.012709 |  | 2 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 3 |  | 11900 | 13.94 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12669026.5903 | ng/dscm | 0.011894 |  | 3 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 13400 | 15.76 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14329683.1043 | ng/dscm | 0.013423 |  | 1 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 12700 | 14.95 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 13586692.8606 | ng/dscm | 0.012709 |  | 2 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 11900 | 13.94 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12669026.5903 | ng/dscm | 0.011894 |  | 3 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 160 | 0.2005 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 182282.1444 | ng/dscm | 0.00015994 | 0.209 | 1 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 | < | 30.7 | 0.03829 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 34804.8877 | ng/dscm | 3.075e-05 | [<.04] | 2 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 | < | 30.5 | 0.03821 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 34735.574 | ng/dscm | 3.0478e-05 | [<0.02] | 3 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 1 |  | 242 | 0.2607 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 236972.3123 | ng/dscm | 0.00024187 |  | 1 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 2 |  | 458 | 0.5523 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 502096.5136 | ng/dscm | 0.00045757 |  | 2 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 3 |  | 233 | 0.291 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 264541.4348 | ng/dscm | 0.00023277 |  | 3 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 1 |  | 237 | 0.301 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 273606.3924 | ng/dscm | 0.00023747 |  | 1 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 2 |  | 208 | 0.2598 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 236155.4534 | ng/dscm | 0.00020779 |  | 2 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 3 |  | 216 | 0.2424 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 220388.5954 | ng/dscm | 0.00021629 |  | 3 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1800 | 2.013 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1830299.2069 | ng/dscm | 0.0017991 |  | M23-1 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 560 | 0.653 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 593609.1077 | ng/dscm | 0.00056004 |  | M23-2 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 464 | 0.5266 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 478731.971 | ng/dscm | 0.00046372 |  | M23-3 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 171 | 0.209 | mg/Nm3 | Poor | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 190019.2365 | ng/dscm | 0.00017073 |  | M29-1 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 216 | 0.2551 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 231880.8252 | ng/dscm | 0.00021595 |  | M29-2 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 197 | 0.2399 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | BDL | 218115.7497 | ng/dscm | 0.00019667 |  | M29-3 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 63.2 | 0.07872 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 71565.2608 | ng/dscm | 6.318e-05 | The value is not blank corrected as the blank value was BDL. | 1 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 231 | 0.2877 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 261577.1267 | ng/dscm | 0.00023093 | The value is not blank corrected as the blank value was BDL. | 2 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 193 | 0.2432 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221070.9363 | ng/dscm | 0.0001931 | The value is not blank corrected as the blank value was BDL. | 3 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 5300 | 6.742 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 6129269.945 | ng/dscm | 0.0053045 | HCl 18700, Blank 0.0 | 1 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 8830 | 11.17 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 10150640.6418 | ng/dscm | 0.0088334 | HCl 31200, Blank 0.0 | 2 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 7650 | 9.632 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 8756238.2107 | ng/dscm | 0.0076487 | HCl 27600, Blank 0.0 | 3 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 179 | 0.2629 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 239007.5188 | ng/dscm | 0.00017906 |  | 1 | 1488
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 134 | 0.1981 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 180058.3702 | ng/dscm | 0.00013411 |  | 2 | 1488
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 128 | 0.1801 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | EPA method 26 | 223 | dscfm | 17.3 % moisture, 15.7 % CO2, 3.7 % O2, 186 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.114 | ppmv | 0.000128 |  | 2 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 179 | 0.2496 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | EPA method 26 | 238050 | dscfm | 15.1 % moisture, 15.5 % CO2, 3.8 % O2, 184 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.158 | ppmv | 0.000179 |  | 1 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 471 | 0.632 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | EPA method 26 | 248616 | dscfm | 15.1 % moisture, 15.3 % CO2, 4.4 % O2, 182 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.4 | ppmv | 0.000471 |  | 1 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 353 | 0.474 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | EPA method 26 | 240230 | dscfm | 16.5 % moisture, 14.4 % CO2, 4.4 % O2, 180 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.3 | ppmv | 0.000353 |  | 2 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 353 | 0.474 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | EPA method 26 | 227964 | dscfm | 17.1 % moisture, 15 % CO2, 4.4 % O2, 180 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.3 | ppmv | 0.000353 |  | 3 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 461 | 0.6532 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 593774.4035 | ng/dscm | 0.00046101 |  | 1 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 376 | 0.5235 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 475882.5115 | ng/dscm | 0.00037632 |  | 3 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 363 | 0.5138 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 467120.108 | ng/dscm | 0.00036267 |  | 2 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 1 |  | 203 | 0.2101 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 190971.3188 | ng/dscm | 0.00020304 |  | 1 | 1978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 2 |  | 157 | 0.1695 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 154051.96 | ng/dscm | 0.00015724 |  | 2 | 1978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 3 |  | 129 | 0.1278 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 116187.4495 | ng/dscm | 0.0001289 |  | 3 | 1978
XX-U-293 | UARG Data Survey from 2009 | Weston Unit 4 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 575 | 525 | Wisconsin Public Service Corp | subbituminous | Northern Great Plains | Power River Basin | Wall-fired | Super critical PC boiler. | 5 |  | 143 | 0.1528 | mg/Nm3 | Good | 2008-07-10 | Ion chromatography (IC) | EPA Method 26A | 1025118 | dscfm | 178F, 14.8% mositure, 13.5% CO2, 8.5% O2
XX-U-293 | UARG Data Survey from 2009 | Weston Unit 4 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 575 | 525 | Wisconsin Public Service Corp | subbituminous | Northern Great Plains | Power River Basin | Wall-fired | Super critical PC boiler. | 6 | < | 39 | 0.04162 | mg/Nm3 | Good | 2008-07-10 | Ion chromatography (IC) | EPA Method 26A | 1025118 | dscfm | 181F, 15.4% mositure, 13.5% CO2, 8.5% O2
XX-U-293 | UARG Data Survey from 2009 | Weston Unit 4 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 575 | 525 | Wisconsin Public Service Corp | subbituminous | Northern Great Plains | Power River Basin | Wall-fired | Super critical PC boiler. | 4 |  | 72 | 0.07687 | mg/Nm3 | Good | 2008-07-10 | Ion chromatography (IC) | EPA Method 26A | 1026809 | dscfm | 180F, 16.7% mositure, 13% CO2, 8.5% O2
XX-U-365 | UARG Data Survey from 2009 | Hayden Unit 1 | NOx: Unspecified, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 286 |  | Xcel Energy | bituminous | Rocky Mountain | Unknown | Wall-fired |  | 1 |  | 39.1 | 0.05 | mg/Nm3 | Good | 2000-12-20 | Method 9057 | Method 26A | 456207 | dscfm | 6.01% O2, 13.51% CO2, 12.1% H2O | Reported as ppmv (dry). Converted to mg/Nm3 using MW/22.414.
XX-U-365 | UARG Data Survey from 2009 | Hayden Unit 1 | NOx: Unspecified, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 286 |  | Xcel Energy | bituminous | Rocky Mountain | Unknown | Wall-fired |  | 2 |  | 23.4 | 0.03 | mg/Nm3 | Good | 2000-12-20 | Method 9057 | Method 26A | 477930 | dscfm | 6.53% O2, 12.19% CO2, 12.4% H2O | Reported as ppmv (dry). Converted to mg/Nm3 using MW/22.414.
XX-U-365 | UARG Data Survey from 2009 | Hayden Unit 1 | NOx: Unspecified, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 286 |  | Xcel Energy | bituminous | Rocky Mountain | Unknown | Wall-fired |  | 3 |  | 23.4 | 0.03 | mg/Nm3 | Good | 2000-12-21 | Method 9057 | Method 26A | 478282 | dscfm | 6.10% O2, 13.04% CO2, 11.1% H2O | Reported as ppmv (dry). Converted to mg/Nm3 using MW/22.414.

## data
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments | Changes to Reported ICR Data | ICR Reported Data Flag | ICR Standardized Data Flag | ICR Reported Concentration | ICR Reported Units of Measure | ICR Emission Factor (lb/million Btu) | ICR Reported Data Comments | ICR Reported Run Number | ICR Submittal ID
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 1 |  | 340 | 0.3633 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 330309.9034 | ng/dscm | 0.00033986 |  | 1 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 2 |  | 293 | 0.3104 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 282154.6187 | ng/dscm | 0.00029267 |  | 2 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 164 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 3 |  | 444 | 0.4637 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 421550.2844 | ng/dscm | 0.00044449 |  | 3 | 5500017
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 1 |  | 472 | 0.5735 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 521337.9605 | ng/dscm | 0.00047174 |  | 1 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 2 |  | 521 | 0.6194 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 563110.0534 | ng/dscm | 0.00052061 |  | 2 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Cayuga, LLC 2535_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 168 |  | AES Cayuga, LLC | bituminous | Eastern | PA, WV | Tangential |  | 3 |  | 406 | 0.4971 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 451941.3767 | ng/dscm | 0.00040606 |  | 3 | 5500018
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 |  | 3010 | 4.021 | mg/Nm3 | Unknown | 2010-04-05 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3655216.6139 | ng/dscm | 0.0030087 |  | 1 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 |  | 2930 | 3.911 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3555859.2254 | ng/dscm | 0.0029269 |  | 2 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 |  | 2750 | 3.649 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 3317663.3714 | ng/dscm | 0.0027486 |  | 3 | 779
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 |  | 1880 | 2.233 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 2030211.0295 | ng/dscm | 0.001877 |  | 1 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 |  | 1660 | 2.003 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 1820545.5275 | ng/dscm | 0.0016591 |  | 2 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 |  | 1950 | 2.349 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 2135765.2558 | ng/dscm | 0.0019464 |  | 3 | 77922
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 138 | 0.1413 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 128464.215 | ng/dscm | 0.00013773 |  | 1 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 174 | 0.1595 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 140890.8728 | ng/dscm | 0.000174 |  | 2 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_1s | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 255 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 | < | 165 | 0.1518 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 133946.3273 | ng/dscm | 0.000165 | <301 | 3 | 636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 187 | 0.192 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 174505.622 | ng/dscm | 0.00018709 |  | 1 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 152 | 0.1597 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 145168.0852 | ng/dscm | 0.00015181 |  | 2 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Petersburg 994_2ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 580 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 148 | 0.1561 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 141932.0196 | ng/dscm | 0.00014843 |  | 3 | 637
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 | < | 113 | 0.1448 | mg/Nm3 | Unknown | 2010-07-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 131674.4376 | ng/dscm | 0.00011275 | [<375] | 1 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 | < | 88.1 | 0.1207 | mg/Nm3 | Unknown | 2010-07-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 109755.8699 | ng/dscm | 8.807e-05 | [<313] | 2 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 | < | 105 | 0.1219 | mg/Nm3 | Unknown | 2010-07-30 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 110826.8834 | ng/dscm | 0.00010474 | [<315] | 3 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 | < | 100 | 0.1321 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 120059.0565 | ng/dscm | 0.00010012 | [<297] | 1 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 | < | 92.5 | 0.1212 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 110198.0179 | ng/dscm | 9.2497e-05 | [<323] | 2 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 | < | 95.3 | 0.1224 | mg/Nm3 | Unknown | 2010-07-28 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 111279.143 | ng/dscm | 9.5285e-05 | [<345] | 3 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 3070 | 4.445 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4040870.6429 | ng/dscm | 0.0030688 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 3520 | 5.124 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4658345.5573 | ng/dscm | 0.0035168 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 3210 | 4.732 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4301557.1123 | ng/dscm | 0.0032094 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 3070 | 4.445 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4040870.6429 | ng/dscm | 0.0030688 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 3520 | 5.124 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4658345.5573 | ng/dscm | 0.0035168 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 3210 | 4.732 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 4301557.1123 | ng/dscm | 0.0032094 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 1 |  | 16100 | 23.24 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21130917.4799 | ng/dscm | 0.016144 |  | 1 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 2 |  | 16400 | 23.15 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21042912.6053 | ng/dscm | 0.01637 |  | 2 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 3 |  | 14400 | 20.8 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 18913247.8355 | ng/dscm | 0.014363 |  | 3 | 1539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 10300 | 12.05 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 10954028.1986 | ng/dscm | 0.010302 |  | 1 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 26600 | 31.26 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 28417639.5337 | ng/dscm | 0.026606 |  | 2 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 24000 | 28.15 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 25589074.037 | ng/dscm | 0.024012 |  | 3 | 1111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 30800 | 36.72 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 33386037.8785 | ng/dscm | 0.030809 |  | 1 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 36000 | 41.5 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 37730723.7419 | ng/dscm | 0.035977 |  | 2 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 32600 | 37.58 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 34167419.0636 | ng/dscm | 0.032614 |  | 3 | 1113
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 1 |  | 432 | 0.5708 | mg/Nm3 | Unknown | 2010-06-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 518877.4387 | ng/dscm | 0.00043213 | Run 1 = 2.42 ug/ml, Blank = 0.928 ug/ml, Vol = 1091 - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 1 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 2 |  | 124 | 0.1655 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 150472.7526 | ng/dscm | 0.00012387 | Run 2 = 1.37ug/ml, Blank = 0.928 ug/ml, Vol = 1051 ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 2 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 48 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 3 |  | 96.6 | 0.1259 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 114484.1333 | ng/dscm | 9.6586e-05 | Run 3 = 1.24ug/ml, Blank = 0.928ug/ml, Vol = 1116ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit" | 3 | 1391
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 1 |  | 22400 | 29.57 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 26882486.9724 | ng/dscm | 0.022384 | Run 1 = 82.5ug/ml, Blank = [ | 1 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 2 |  | 1510 | 1.942 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1765815.221 | ng/dscm | 0.0015078 | Run 2 = 5.86ug/ml, Blank = [ | 2 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 3 |  | 310 | 0.3794 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 344904.8208 | ng/dscm | 0.00030995 | Run 3 = 2.34ug/ml, Blank = 1.59ug/ml, Vol = 1369 ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit." | 3 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Arapahoe 465_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 118 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Vertical-fired |  | 4 |  | 399 | 0.5358 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 487049.3707 | ng/dscm | 0.00039946 | Run 4 = 2.74ug/ml, Blank = 1.59ug/ml, Vol = 1270ml - MDL for HCl and HF determined using procedures found in 40 CFR Part 136 App B "Determination of the Method Detection Limit." | 4 | 1396
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 7210 | 9.379 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 8526442.9751 | ng/dscm | 0.0072143 | 26361, Blank N/D | 2 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 4430 | 5.799 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5272165.2859 | ng/dscm | 0.0044343 | 16234, Blank N/D | 3 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 6760 | 8.639 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 7853282.4702 | ng/dscm | 0.0067582 | 32174, Blank N/D | 1 | 1738
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 1 |  | 600 | 0.7428 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.3558 | ng/dscm | 0.00060024 | HCl 2360, Blank 266 | 1 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 2 |  | 601 | 0.7387 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 671563.0597 | ng/dscm | 0.00060077 | HCl 2400, Blank 266 | 2 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 176 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 3 |  | 525 | 0.6465 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 587726.0108 | ng/dscm | 0.00052458 | HCl 2130, Blank 266 | 3 | 1912
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 1 |  | 600 | 0.7428 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.3558 | ng/dscm | 0.00060024 | HCl 2360, Blank 266 | 1 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 2 |  | 601 | 0.7387 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 671563.0597 | ng/dscm | 0.00060077 | HCl 2400, Blank 266 | 2 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bailly 995_8 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Packed,Forced ox), SO3: SI | Coal-Fired Boilers | 352 |  | Northern Indiana Public Service Company | bituminous | Interior(East, North) | IL, IN | Cyclone |  | 3 |  | 525 | 0.6465 | mg/Nm3 | Unknown | 2010-07-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 587726.0108 | ng/dscm | 0.00052458 | HCl 2130, Blank 266 | 3 | 1910
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 5 |  | 752 | 0.9609 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 873511.378 | ng/dscm | 0.000752 | 700, 239 | M26A-5 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 4 |  | 832 | 1.065 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | ADL | 967835.2236 | ng/dscm | 0.00083152 | 892, 159 - backup impinger amount was coded "B" indicating the amount detected was a positive result less than the reporting limit but greater than the MDL. | M26A-4 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Belews Creek Steam Station 8042_1-2008 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 1186 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 317 | 0.4052 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | DLL | BDL | 368337.7846 | ng/dscm | 0.0003171 | [ | M26A-3 | 911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 4 | UNK | 1040 | 1.413 | mg/Nm3 | Poor | 2010-04-22 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1284749.447 | ng/dscm | 0.0010374 |  | 4 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 9170 | 10.99 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 9988333.698 | ng/dscm | 0.0091681 |  | 1 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB01_pre-SCR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 1160 | 1.442 | mg/Nm3 | Poor | 2010-04-22 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1310995.8666 | ng/dscm | 0.0011615 |  | 3 | 1757
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 7560 | 7.755 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 7050038.887 | ng/dscm | 0.0075586 |  | 2 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 5320 | 6.379 | mg/Nm3 | Poor | 2010-03-11 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 5798764.6844 | ng/dscm | 0.0053225 |  | 3 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Bend 645_BB02_SCR | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 410 |  | Tampa Electric | bituminous | Eastern | KY | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 6140 | 6.295 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 5722344.4939 | ng/dscm | 0.0061352 |  | 1 | 1758
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 1 |  | 60.6 | 0.06967 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 523536 | dscfm | 6.23 % O2, 60.83 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.0441 | ppmv | 0.0022 |  | 2017-01-01 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 2 |  | 65.5 | 0.0752 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 523536 | dscfm | 6.23 % O2, 62.46 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.0476 | ppmv | 0.0003 |  | 2017-01-02 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 3 | < | 70.1 | 0.08057 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 528024 | dscfm | 6.29 % O2, 60.08 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.051 | ppmv | 0.0001 |  | 2017-01-03 | 1053
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 |  | 990 | 1.237 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1124798.6213 | ng/dscm | 0.00098971 |  | M26A-1 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 1030 | 1.292 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1174558.1518 | ng/dscm | 0.0010335 |  | M26A-2 | 654465454
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 |  | 1000 | 1.192 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | EPA method 26 | 369719 | dscfm | 16.98 % moisture, 13.1 % CO2, 6.4 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.75436 | ppmv | 0.001 | [200] | 1 | 90000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | BL England 2378_2 Coal w or w/o TDF | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 300 |  | RC Cape May Holdings LLC | bituminous | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 1000 | 1.245 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | EPA method 26 | 391635 | dscfm | 16.97 % moisture, 13 % CO2, 6.4 % O2, 127 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.78775 | ppmv | 0.001 | [200] | 2 | 90000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 535 | 0.6749 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 613553.9487 | ng/dscm | 0.0005347 | [<1600] | 1 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 497 | 0.6228 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 566182.9141 | ng/dscm | 0.00049679 | [<1500] | 2 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Boswell Energy Center 1893_BEC3 | NOx: SCR, PM: FF, SO2: FGDw(Spray,Natural), Hg: ACSI | Coal-Fired Boilers | 371 |  | Allette, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 507 | 0.6393 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 581214.2089 | ng/dscm | 0.00050651 | [<1500] | 3 | 2172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 224 | 0.2533 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 230232.9558 | ng/dscm | 0.00022423 |  | 1 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 137 | 0.1583 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 143952.0742 | ng/dscm | 0.00013706 |  | 2 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 755 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 106 | 0.1212 | mg/Nm3 | Poor | 2010-02-23 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | ADL | ADL | 110194.1899 | ng/dscm | 0.00010571 |  | 3 | 1986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 228 | 0.2841 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 258235.4631 | ng/dscm | 0.00022801 |  | 1 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 269 | 0.3254 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 295806.3528 | ng/dscm | 0.00026861 |  | 2 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 252 | 0.3075 | mg/Nm3 | Poor | 2010-02-24 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 279510.7914 | ng/dscm | 0.00025202 |  | 3 | 19861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 103 | 0.1289 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 117139.1492 | ng/dscm | 0.00010343 |  | 1 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 81.9 | 0.1024 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 93081.4658 | ng/dscm | 8.1902e-05 |  | 2 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bowen 703_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 933 |  | Georgia Power | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 173 | 0.222 | mg/Nm3 | Poor | 2010-02-25 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. |  | adl | adl | 201857.897 | ng/dscm | 0.00017285 |  | 3 | 19862
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2010 | 2.893 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 2630076.2804 | ng/dscm | 0.0020093 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 1 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 901 | 1.297 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 1179153.7813 | ng/dscm | 0.00090085 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 2 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2790 | 4.014 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | BDL | ADL | 3649065.9816 | ng/dscm | 0.0027878 | RDL = 200 ug, MDL=60 ug; Hydrochloric acid | 3 | 1618
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 145 | 0.1726 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 156921.1118 | ng/dscm | 0.00014466 |  | M26A-1 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 119 | 0.1437 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 130609.2262 | ng/dscm | 0.00011937 |  | M26A-2 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 165 | 0.1936 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 175990.6738 | ng/dscm | 0.00016486 |  | M26A-3 | 549
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 144 | 0.1743 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 158471.7465 | ng/dscm | 0.00014442 |  | M26A-1 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 247 | 0.2982 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 271134.5719 | ng/dscm | 0.00024709 |  | M26A-2 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 615 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 165 | 0.1986 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 180578.8562 | ng/dscm | 0.00016457 |  | M26A-3 | 550001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 34300 | 37.26 | mg/Nm3 | Poor | 2010-05-18 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 33875239.1616 | ng/dscm | 0.034301 |  | M29-1 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 33300 | 36.2 | mg/Nm3 | Poor | 2010-05-19 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 32905123.1855 | ng/dscm | 0.033319 |  | M29-2 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 35800 | 38.88 | mg/Nm3 | Poor | 2010-05-21 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 35349848.2739 | ng/dscm | 0.035794 |  | M29-3 | 1004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 23000 | 34.64 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 31487650.351 | ng/dscm | 0.022956 |  | 1 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 58100 | 87.62 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 79652011.1421 | ng/dscm | 0.058071 |  | 2 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 46600 | 70.31 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 63919017.891 | ng/dscm | 0.046601 |  | M5-3 | 2198
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 21500 | 24.65 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 221236 | dscfm | 6.7 % moisture, 13.5 % CO2, 5.2 % O2, 329 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.021491 |  | 1 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 53300 | 61.3 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 214647 | dscfm | 7.5 % moisture, 13.8 % CO2, 4.9 % O2, 331.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.053314 |  | 2 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 45900 | 52.77 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 26A-Mod | 211618 | dscfm | 7.5 % moisture, 13.8 % CO2, 5 % O2, 330.6 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.04588 |  | 3 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 50500 | 57.98 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 243429 | dscfm | 9.67 % moisture, 13.4 % CO2, 5.24 % O2, 312.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050479 |  | 1 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 39700 | 45.66 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 238673 | dscfm | 9.3 % moisture, 13.5 % CO2, 5.17 % O2, 318.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.039739 |  | 2 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 57500 | 66.04 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 26A-Mod | 252861 | dscfm | 9.46 % moisture, 13.5 % CO2, 5.17 % O2, 318.4 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.057522 |  | 3 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 50900 | 76.79 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 69812159.5852 | ng/dscm | 0.050897 |  | 1 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 40100 | 60.57 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 55060878.2362 | ng/dscm | 0.040142 |  | 2 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 58600 | 88.41 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 80375190.6046 | ng/dscm | 0.058598 |  | M5-3 | 2199
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 48900 | 73.77 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 67061303.5077 | ng/dscm | 0.048891 |  | 1 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 49500 | 74.75 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 67953498.3107 | ng/dscm | 0.049542 |  | 2 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 50700 | 76.47 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 69518965.3244 | ng/dscm | 0.050683 |  | M5-3 | 2200
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 49100 | 56.4 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 223578 | dscfm | 9.2 % moisture, 13.1 % CO2, 5.44 % O2, 310.5 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.049067 |  | 1 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 50300 | 57.82 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 231515 | dscfm | 9.3 % moisture, 13 % CO2, 5.59 % O2, 313.8 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050302 |  | 2 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 50600 | 58.14 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 | 223095 | dscfm | 9.7 % moisture, 13 % CO2, 5.5 % O2, 316.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.050585 |  | 3 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 76 | 0.105 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 95497.0683 | ng/dscm | 7.6046e-05 |  | 1 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 30.8 | 0.04254 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 38672.6418 | ng/dscm | 3.0756e-05 | above detection level | 2 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 20.4 | 0.02805 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 25499.9639 | ng/dscm | 2.0397e-05 | above detection limit | 3 | 1128
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 88.4 | 0.1244 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 113101.2757 | ng/dscm | 8.8371e-05 |  | 1 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 36.1 | 0.05191 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 47193.6198 | ng/dscm | 3.6062e-05 |  | 2 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 43.6 | 0.06345 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 57679.1838 | ng/dscm | 4.3594e-05 |  | 3 | 1365
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 2 |  | 270 | 0.3356 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 305046.6296 | ng/dscm | 0.00026965 | Blank = | 2 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 3 |  | 159 | 0.2029 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 184469.1855 | ng/dscm | 0.00015929 | Blank = | 3 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 117 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 4 |  | 247 | 0.3252 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 295628.5104 | ng/dscm | 0.00024718 | Blank = | 4 | 1403
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 1 |  | 200 | 0.2696 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 245122.2647 | ng/dscm | 0.00019951 | Blank = | 1 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 2 |  | 185 | 0.2504 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 227591.5684 | ng/dscm | 0.00018507 | Blank = | 2 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDdsi | Coal-Fired Boilers | 114 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Vertical-fired |  | 3 |  | 175 | 0.2409 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 219016.8995 | ng/dscm | 0.00017452 | Blank = | 3 | 1433
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 241 | 0.2952 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 268359.438 | ng/dscm | 0.00024078 | Blank = | 1 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 203 | 0.2431 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221030.9063 | ng/dscm | 0.00020283 | Blank = | 2 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 3 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 165 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 473 | 0.5631 | mg/Nm3 | Unknown | 2010-03-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 511941.4703 | ng/dscm | 0.0004726 | Blank = | 3 | 1436
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 319 | 0.4245 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 385940.0936 | ng/dscm | 0.00031908 | Blank = | 1 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 194 | 0.2625 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 238606.2222 | ng/dscm | 0.00019412 | Blank = | 2 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cherokee 469_Unit 4 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 383 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 197 | 0.2589 | mg/Nm3 | Unknown | 2010-03-24 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 235406.4554 | ng/dscm | 0.00019732 | Blank = | 3 | 1442
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 | < | 80.2 | 0.1123 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 102091.8531 | ng/dscm | 8.0156e-05 | [ | 3 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 | < | 81.3 | 0.1134 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 103052.2101 | ng/dscm | 8.131e-05 | [ | 1 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 | < | 79.4 | 0.1105 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 100450.606 | ng/dscm | 7.9356e-05 | [ | 2 | 1647
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 | < | 87.4 | 0.1167 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 106086.3318 | ng/dscm | 8.7379e-05 | [ | R3 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 | < | 83.6 | 0.112 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 101842.9776 | ng/dscm | 8.3614e-05 | [ | R1 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 | < | 84.7 | 0.1135 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 103195.2825 | ng/dscm | 8.4724e-05 | [ | R2 | 1648
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 3 | UNK | 33000 | 45.48 | mg/Nm3 | Poor | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 41343394.5646 | ng/dscm | 0.032967 |  | M29-3 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 1 | UNK | 19600 | 17.98 | mg/Nm3 | Poor | 2010-05-11 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 16349504.3298 | ng/dscm | 0.0196 |  | M29-1 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 2 | UNK | 18500 | 17.13 | mg/Nm3 | Poor | 2010-05-12 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 15575454.529 | ng/dscm | 0.0185 |  | M29-2 | 10040002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 355 | 0.4513 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 410247.309 | ng/dscm | 0.00035512 |  | 1 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 426 | 0.5336 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 485130.1275 | ng/dscm | 0.00042636 |  | 3 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 338 | 0.4266 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 387823.4487 | ng/dscm | 0.00033773 |  | 2 | 1534
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 300 | 0.4061 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 369225.9224 | ng/dscm | 0.00030005 |  | 1 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 395 | 0.511 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 464527.7403 | ng/dscm | 0.00039511 |  | 2 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 318 | 0.4083 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 371149.696 | ng/dscm | 0.00031781 |  | 3 | 1535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1310 | 1.619 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1471728.094 | ng/dscm | 0.0013131 |  | 1 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1980 | 2.384 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 2167219.2907 | ng/dscm | 0.001975 |  | 2 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Coffeen 861_001 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 360 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1270 | 1.593 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1448276.5761 | ng/dscm | 0.0012656 |  | 3 | 1807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 3 |  | 9420 | 12.66 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 11504614.4405 | ng/dscm | 0.0094151 |  | 3 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 1 |  | 5100 | 6.849 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 6225957.2026 | ng/dscm | 0.0051017 |  | 1 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 2 |  | 696 | 0.9339 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 849038.4615 | ng/dscm | 0.00069573 |  | 2 | 1302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 1 |  | 433 | 0.5916 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 537799.7716 | ng/dscm | 0.00043345 |  | 1 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 2 |  | 235 | 0.3068 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 278905.2259 | ng/dscm | 0.00023488 |  | 2 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cogentrix Virginia Leasing Corporation 10071_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | Cogentrix-Virginia Leas'g Corp | bituminous | Eastern | WV | Stoker | Underfeed stoker boiler. | 3 |  | 276 | 0.3583 | mg/Nm3 | Unknown | 2010-04-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 325727.592 | ng/dscm | 0.00027595 |  | 3 | 1303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 14600 | 16.45 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14956557.2307 | ng/dscm | 0.014567 | 66400 | 1 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 16000 | 18.25 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 16592782.4044 | ng/dscm | 0.016001 | 72600 | 2 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 10400 | 11.53 | mg/Nm3 | Unknown | 2010-05-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 10478398.8886 | ng/dscm | 0.010355 | 45700 | 3 | 2274
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 80.2 | 0.09791 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 89008.1802 | ng/dscm | 8.0187e-05 | Analytical result between the MDL and the LOQ, value should be considered an estimate. Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does no | 1 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 50 | 0.06128 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 55708.8814 | ng/dscm | 4.9977e-05 | Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does not meet the criteria of 40 CFR Part 136 B, MDL = 1/10 the concentration of the standard u | 2 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 56.1 | 0.06949 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 63168.5838 | ng/dscm | 5.6119e-05 | Lab MDL = Student t factor multiplied by std. deviation of the analysis of at least 7 replicate standards at a concentration near the expected MDL. If the MDL does not meet the criteria of 40 CFR Part 136 B, MDL = 1/10 the concentration of the standard u | 3 | 1558
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 36700 | 49.15 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 44684957.6536 | ng/dscm | 0.036665 |  | 1 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27600 | 36.22 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 32926912.745 | ng/dscm | 0.027628 |  | 2 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 31800 | 40.99 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 37263211.3771 | ng/dscm | 0.031787 |  | 3 | 1293
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 36700 | 46.56 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 26A-Mod | 273787 | dscfm | 7.4 % moisture, 14.62 % CO2, 5.15 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 29.47 | ppmv | 0.0367 |  | 1 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27600 | 34.3 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 26A-Mod | 280046 | dscfm | 7.32 % moisture, 14.83 % CO2, 5.01 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 21.71 | ppmv | 0.0276 |  | 2 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 31800 | 38.82 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 26A-Mod | 277907 | dscfm | 7.19 % moisture, 14.77 % CO2, 5.06 % O2, 316 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 24.57 | ppmv | 0.0318 |  | 3 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 1 |  | 305 | 0.3714 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 337641.9869 | ng/dscm | 0.00030527 | ADL Sample 1 1794, BDL Sample 2 [<260] | 1 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 2 |  | 296 | 0.3647 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 331568.6924 | ng/dscm | 0.00029589 | ADL Sample 1 731, ADL Sample 2 [<170] | 2 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 3 |  | 263 | 0.3253 | mg/Nm3 | Poor | 2010-03-11 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 295772.289 | ng/dscm | 0.00026289 | ADL Sample 1 755, BDL Sample 2 [<65] | 3 | 473
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 1 |  | 421 | 0.5277 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 479687.9773 | ng/dscm | 0.0004206 | ADL Sample 1 977, ADL Sample 2 527 BDL Sample 3 [<150] | 1 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 2 |  | 279 | 0.3523 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 320246.7012 | ng/dscm | 0.00027912 | ADL Sample 1 817, BDL Sample 2 [<120] | 2 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conemaugh 3118_CON-2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 936 |  | Conemaugh Owners Group | bituminous | Eastern | Unknown | Tangential |  | 3 |  | 298 | 0.3757 | mg/Nm3 | Poor | 2010-03-10 | Not Specified | EPA method 26A |  |  |  | Samples collected using dual train for HCN. Detection limit higher than normal. Laboratory confirmed analytical issues. |  | DLL | DLL | 341564.385 | ng/dscm | 0.00029827 | ADL Sample 1 768, BDL Sample 2 [<240] | 3 | 466
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 1 |  | 33400 | 34.56 | mg/Nm3 | Unknown | 2010-06-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 31422725.1037 | ng/dscm | 0.033409 |  | M29-1 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 2 |  | 39000 | 39.65 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 36043156.7913 | ng/dscm | 0.038971 |  | M29-2 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 3 |  | 34900 | 35.25 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 32043470.7871 | ng/dscm | 0.034942 |  | M29-3 | 1286
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 1 | UNK | 155 | 0.1899 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 172600.0621 | ng/dscm | 0.00015508 |  | M26A-1 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 2 | UNK | 146 | 0.1785 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 162303.5344 | ng/dscm | 0.00014583 |  | M26A-2 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Jet Bubble Reactor), SO3: SI | Coal-Fired Boilers | 842 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Tangential |  | 3 | UNK | 189 | 0.2376 | mg/Nm3 | Poor | 2010-04-27 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 215978.7389 | ng/dscm | 0.00018874 |  | M26A-3 | 550002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 1 |  | 340 | 0.3694 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 335802.643 | ng/dscm | 0.0003403 |  | 1 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 2 |  | 229 | 0.2479 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 225408.5024 | ng/dscm | 0.00022915 |  | 2 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 3 |  | 162 | 0.173 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 157242.9181 | ng/dscm | 0.00016179 |  | 3 | 1117
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 59 | 0.08133 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 73936.8677 | ng/dscm | 5.9031e-05 |  | 1 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 71 | 0.09783 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 88935.9398 | ng/dscm | 7.0962e-05 |  | 2 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 76.8 | 0.1063 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 96645.7278 | ng/dscm | 7.6826e-05 |  | 3 | 1118
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 247 | 0.328 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 298139.4268 | ng/dscm | 0.00024684 |  | 1 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 155 | 0.2005 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 182274.6755 | ng/dscm | 0.00015452 |  | 2 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 286 | 0.3698 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 336166.3375 | ng/dscm | 0.00028555 |  | 3 | 1119
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 50500 | 62.91 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 57194260.2354 | ng/dscm | 0.050472 | 241147, Blank H20 [<85.2] | M29-1 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 87400 | 109.4 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 99429728.8974 | ng/dscm | 0.087372 | 416811, Blank H20 [<85.2] | M29-2 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 85200 | 106.3 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | No duplicates performed as required by method. No spikes performed to validate data and rule out any matrix interference. No calibration data from lab was received to validate data. |  | ADL | ADL | 96609075.1901 | ng/dscm | 0.085213 | 409396, Blank H20 [<85.2] | M29-3 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 217 | 0.2701 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 245569.1969 | ng/dscm | 0.00021708 | 790, Blank H2O [<78.8] | M26A-1 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 440 | 0.5474 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 497622.2891 | ng/dscm | 0.00044029 | 1602, Blank H2O [<78.8] | M26A-2 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_5c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray), SO3: SI | Coal-Fired Boilers | 767 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 164 | 0.2054 | mg/Nm3 | Unknown | 2010-03-29 | Not Specified | EPA method 26A | [5 empty] | adl | adl | 186706.2167 | ng/dscm | 0.00016416 | 597, Blank H20 [<78.8] | M26A-3 | 978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 1 |  | 308 | 0.4078 | mg/Nm3 | Unknown | 2010-06-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 370701.1281 | ng/dscm | 0.00030772 | 882 | 1 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 2 |  | 310 | 0.4133 | mg/Nm3 | Unknown | 2010-06-25 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 375764.4704 | ng/dscm | 0.00031042 | 1010 | 2 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cumberland 3399_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1300 |  | Tennessee Valley Authority | bituminous | Interior(East, North) | IL, KY | Wall-fired | Opposed wall-fired boiler. | 3 |  | 386 | 0.4978 | mg/Nm3 | Unknown | 2010-06-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 452584.6442 | ng/dscm | 0.00038598 | 1230 | 3 | 2166
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 142000 | 153.4 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 139499768.3409 | ng/dscm | 0.14238 |  | M29-1 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 148000 | 160 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 145426264.3823 | ng/dscm | 0.14843 |  | M29-2 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 141000 | 153.3 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 139395789.7402 | ng/dscm | 0.14115 |  | M29-3 | 993
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 142000 | 164.3 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26 | 202947 | dscfm | 8.4 % moisture, 10.205475 % CO2, 8.2482563019 % O2, 279.221775 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 93.56 | ppmv | 0.1424 | [5000] | 1 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 149000 | 170.6 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | EPA method 26 | 201486 | dscfm | 8.4 % moisture, 10.185575 % CO2, 8.2729263637 % O2, 298.894075 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 97.53 | ppmv | 0.1485 | [5000] | 2 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 141000 | 164.3 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | EPA method 26 | 203278 | dscfm | 8.4 % moisture, 10.2312 % CO2, 8.2163649782 % O2, 287.949375 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 93.49 | ppmv | 0.1412 | [5000] | 3 | 996001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 1 | < | 65 | 0.07899 | mg/Nm3 | Poor | 2010-06-30 | Unknown | Unknown | 399610 | dscfm | 15.1 % moisture, 12 % CO2, 6.8 % O2, 129.3 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | [<0.05] | ppmv | [<0.000065] |  | 1 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 136 | 0.158 | mg/Nm3 | Unknown | 2010-07-01 | Unknown | Unknown | 391001 | dscfm | 15.4 % moisture, 11.7 % CO2, 7 % O2, 130.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DDL | DLL | 0.1 | ppmv | 0.000136 |  | 2 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 100 | 0.1264 | mg/Nm3 | Unknown | 2010-07-01 | Unknown | Unknown | 384158 | dscfm | 14.9 % moisture, 11.2 % CO2, 7.6 % O2, 128.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DDL | DLL | 0.08 | ppmv | 0.0001 |  | 3 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 1 | < | 180 | 0.2216 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | BDL | 201484.3256 | ng/dscm | 0.00017976 | [0.2291] | 1 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 2 |  | 540 | 0.6708 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 609837.5098 | ng/dscm | 0.00054032 |  | 2 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 3 |  | 784 | 0.9668 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 878873.3322 | ng/dscm | 0.00078413 |  | 3 | 2239
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 677 | 0.8184 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 744008.2387 | ng/dscm | 0.00067726 | ADL | 1 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 947 | 1.145 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1040619.6454 | ng/dscm | 0.00094711 | ADL | 2 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1120 | 1.359 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1235694.7382 | ng/dscm | 0.001116 | ADL | 3 | 535
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 811 | 0.9583 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 871162.0321 | ng/dscm | 0.00081137 | ADL | 1 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 999 | 1.191 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1082916.0148 | ng/dscm | 0.00099895 | ADL | 2 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1090 | 1.3 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26 | [5 empty] | ADL | ADL | 1182218.0015 | ng/dscm | 0.0010905 | ADL | 3 | 536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 522 | 0.553 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 502748.7744 | ng/dscm | 0.00052234 |  | 1 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 585 | 0.619 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 562718.2641 | ng/dscm | 0.00058512 |  | 2 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 478 | 0.5052 | mg/Nm3 | Unknown | 2010-07-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 459235.542 | ng/dscm | 0.00047791 |  | 3 | 2055
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 53500 | 55.36 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 50327764.8906 | ng/dscm | 0.053509 |  | U1-M29-1 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 38500 | 41.13 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 37393326.9944 | ng/dscm | 0.038474 |  | U1-M29-3 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 53200 | 53.68 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 48799177.8423 | ng/dscm | 0.053214 |  | U1-M29-2 | 2279
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 5 |  | 63800 | 61.62 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 56016430.4499 | ng/dscm | 0.063811 |  | U3-26A-5 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 6 |  | 63400 | 62.33 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 56668005.4536 | ng/dscm | 0.063421 |  | U3-26A-6 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 4 |  | 63900 | 61.12 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 55559372.9114 | ng/dscm | 0.063861 |  | U3-26A-4 | 22791
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 579 | 0.6341 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 576440.3407 | ng/dscm | 0.00057909 |  | 1 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 803 | 0.8728 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 793416.7698 | ng/dscm | 0.0008034 |  | 2 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 444 | 0.4781 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 434652.178 | ng/dscm | 0.00044364 |  | 3 | 1847
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 88.6 | 0.1238 | mg/Nm3 | Unknown | 2010-11-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 112555.768 | ng/dscm | 8.8645e-05 | See report for detection limit explanation. | M29-1 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 84 | 0.1196 | mg/Nm3 | Unknown | 2010-11-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 108696.8094 | ng/dscm | 8.4049e-05 | See report for detection limit explanation. | M29-2 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 56.5 | 0.07941 | mg/Nm3 | Unknown | 2010-11-09 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 72194.7869 | ng/dscm | 5.6509e-05 | See report for detection limit explanation. | M29-3 | 2319
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 321 | 0.3845 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 349527.8768 | ng/dscm | 0.00032087 | 1510, [<170] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 320 | 0.3839 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 349026.7603 | ng/dscm | 0.00032041 | 1410, 210 | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 341 | 0.4085 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A |  |  |  |  | Re-calculated EF from concentration. | DLL | DLL | 371396.2963 | ng/dscm | 0.00034094 | 1590, [<160] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 186000 | 269 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 244544575.3473 | ng/dscm | 0.18568 |  | M29-1 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 178000 | 250.1 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 227326897.1245 | ng/dscm | 0.17772 |  | M29-2 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 170000 | 241.5 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 219552230.9435 | ng/dscm | 0.17013 |  | M29-3 | 1845
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_1-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_2-2009 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 177 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1010 | 1.331 | mg/Nm3 | Unknown | 2010-03-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1210001.8376 | ng/dscm | 0.0010097 | 935, 370 ug | M29- R1 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1180 | 1.562 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1420276.1114 | ng/dscm | 0.0011767 | 1160, 375 ug | M29-R2 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 991 | 1.326 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1205439.1138 | ng/dscm | 0.00099095 | 1040, 291 ug | M29-R3 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1010 | 1.331 | mg/Nm3 | Unknown | 2010-03-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1210001.8376 | ng/dscm | 0.0010097 | 935, 370 ug | M29- R1 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1180 | 1.562 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1420276.1114 | ng/dscm | 0.0011767 | 1160, 375 ug | M29-R2 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 991 | 1.326 | mg/Nm3 | Unknown | 2010-03-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1205439.1138 | ng/dscm | 0.00099095 | 1040, 291 ug | M29-R3 | 900
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 1120 | 1.422 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1292842.4216 | ng/dscm | 0.0011229 | 1340, 365 | 1 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 1130 | 1.435 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1304386.9401 | ng/dscm | 0.0011337 | 1410, 324 | 2 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_5-2009 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 285.3 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 1170 | 1.484 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1349065.1238 | ng/dscm | 0.0011717 | 1460, 296 | 3 | 898
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2030 | 2.169 | mg/Nm3 | Unknown | 2010-02-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1972136.1319 | ng/dscm | 0.0020275 | 4940 | 1 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1310 | 1.386 | mg/Nm3 | Unknown | 2010-02-24 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 1259996.2957 | ng/dscm | 0.001307 | 3880, [<550] | 2 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1340 | 1.421 | mg/Nm3 | Unknown | 2010-02-25 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 1292003.4932 | ng/dscm | 0.0013402 | 3910. [<530] | 3 | 2278
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 1 |  | 125 | 0.1479 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 134443.8016 | ng/dscm | 0.0001252 |  | M26A-1 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 2 |  | 188 | 0.2207 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 200667.2008 | ng/dscm | 0.00018825 |  | M26A-2 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 520 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Tangential |  | 3 |  | 225 | 0.2526 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 229627.3287 | ng/dscm | 0.00022536 |  | M26A-3 | 1656
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 626 | 0.7245 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 658605.0328 | ng/dscm | 0.00062567 |  | M26A-1 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 589 | 0.6809 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 619037.516 | ng/dscm | 0.00058896 |  | M26A-2 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH3 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 365 | 0.4236 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 385099.0369 | ng/dscm | 0.00036503 |  | M26A-3 | 16561
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 604 | 0.5768 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 524350.5002 | ng/dscm | 0.00060378 |  | M26A-1 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 829 | 0.816 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 741855.5805 | ng/dscm | 0.0008288 |  | M26A-2 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ghent 1356_GH4 | NOx: SCR, PM: ESPh(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 525 |  | Kentucky Utilities Co. | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 657 | 0.6614 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 601267.1344 | ng/dscm | 0.00065735 |  | M26A-3 | 165611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 | < | 269 | 0.3421 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 310970.2412 | ng/dscm | 0.00026898 | [ | 1 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 | < | 256 | 0.3265 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 296780.4705 | ng/dscm | 0.00025602 | [ | 2 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Inhibited), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 | < | 257 | 0.3269 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 297210.1754 | ng/dscm | 0.00025673 | [ | 3 | 1639
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 27400 | 29.82 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 27108070.3326 | ng/dscm | 0.027449 |  | M29-2 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 26200 | 28.86 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 26238117.8352 | ng/dscm | 0.026153 |  | M29-3 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 19000 | 20.91 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19012438.3331 | ng/dscm | 0.018951 |  | M29-1 | 1974
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 56.4 | 0.07686 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 69875.2849 | ng/dscm | 5.6424e-05 | [ | M29-1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 111 | 0.1512 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 137461.9931 | ng/dscm | 0.000111 |  | M29-2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 58 | 0.07897 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 71793.2874 | ng/dscm | 5.7973e-05 | [ | M29-3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 | < | 50 | 0.07425 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | EPA method 26 | 33509979 | dscfm | 10.9 % moisture, 12.922825 % CO2, 4.4300675899 % O2, 166.89105 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.047 | ppmv | [<.00005] | [250] | 1 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 110 | 0.1453 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26 | 33768324 | dscfm | 10.9 % moisture, 12.940675 % CO2, 4.4073062648 % O2, 166.671625 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.092 | ppmv | 0.00011 | [250] | 2 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 | < | 60 | 0.07425 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | EPA method 26 | 33693766 | dscfm | 10.9 % moisture, 12.902275 % CO2, 4.4562209265 % O2, 167.349325 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.047 | ppmv | [<.00006] | [250] | 3 | 1563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 132 | 0.1798 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 163477.8733 | ng/dscm | 0.00013201 |  | M29-1 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 123 | 0.1664 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 151244.6988 | ng/dscm | 0.00012291 |  | M29-2 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 136 | 0.1838 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 167112.564 | ng/dscm | 0.0001358 |  | M29-3 | 995
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 541963 | dscfm | 11.1 % moisture, 12.91349858 % CO2, 4.4049060321 % O2, 245.3452786 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1096 | ppmv | 0.0002 | [200] | 1 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 541225 | dscfm | 11.1 % moisture, 12.8878421 % CO2, 4.4376784094 % O2, 244.6899624 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1025 | ppmv | 0.0002 | [200] | 2 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 200 | 0.2291 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 540995 | dscfm | 11.1 % moisture, 12.88162946 % CO2, 4.4456141427 % O2, 244.9691296 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.1119 | ppmv | 0.0002 | [200] | 3 | 998001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 1 |  | 102 | 0.1073 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 97519.2061 | ng/dscm | 0.00010249 | HCl 308, Blank N/D | 1 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 2 |  | 128 | 0.1417 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 128783.9175 | ng/dscm | 0.00012805 | HCl 446, Blank ND | 2 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hamilton 2917_Unit 9 | NOx: Unspecified, PM: ESPh(Without Conditioning) FFp, SO2: FGDsd | Coal-Fired Boilers | 51 |  | City of Hamilton | bituminous | Eastern | OH, WV | Tangential |  | 3 | < | 100 | 0.1081 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 98272.9495 | ng/dscm | 0.00010004 | HCl [ | 3 | 1929
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 90.1 | 0.09165 | mg/Nm3 | Unknown | 2010-02-02 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83321.9392 | ng/dscm | 9.009e-05 |  | 1 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 64.2 | 0.0639 | mg/Nm3 | Unknown | 2010-02-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 58087.8486 | ng/dscm | 6.4166e-05 |  | 2 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 82 | 0.08241 | mg/Nm3 | Unknown | 2010-02-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 74916.269 | ng/dscm | 8.2044e-05 |  | 3 | 1984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 | < | 144 | 0.1848 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 167966.5208 | ng/dscm | 0.00014383 |  | 29-1 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 146 | 0.1895 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 172297.6076 | ng/dscm | 0.00014558 |  | 29-2 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hardin Generator Project 55749_PC1 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 119 |  | Rocky Mountain Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 | < | 147 | 0.1864 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 169494.7789 | ng/dscm | 0.00014711 |  | 29-3 | 2112
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1150 | 1.321 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 1201320.8731 | ng/dscm | 0.0011515 |  | 1 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 372 | 0.4413 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 401195.8979 | ng/dscm | 0.000372 |  | 2 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 693 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 281 | 0.3214 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 292214.4622 | ng/dscm | 0.00028116 |  | 3 | 1109
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 980 | 1.088 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 989202.4132 | ng/dscm | 0.00097987 |  | 1 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 634 | 0.7371 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 670047.0431 | ng/dscm | 0.00063371 |  | 2 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 357 | 0.4246 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 385985.6184 | ng/dscm | 0.00035685 |  | 3 | 11091
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 660 | 0.7658 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 696146.2655 | ng/dscm | 0.00066035 |  | 1 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 635 | 0.7375 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 670461.6853 | ng/dscm | 0.00063458 |  | 2 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harrison Power Station 3944_Boiler3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 692 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 567 | 0.6627 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 602428.0124 | ng/dscm | 0.00056682 |  | 3 | 110911
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 132 | 0.1851 | mg/Nm3 | Unknown | 2010-05-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 168270.6051 | ng/dscm | 0.00013241 |  | 1 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 134 | 0.1882 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 171064.3574 | ng/dscm | 0.00013436 |  | 2 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 127 | 0.1795 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 163217.8375 | ng/dscm | 0.00012711 |  | 3 | 1120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | < | 68.1 | 0.08929 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81170.2361 | ng/dscm | 6.8132e-05 | ND, MDL Listed | 1 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | < | 73.4 | 0.09624 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 87492.8848 | ng/dscm | 7.3439e-05 | ND, MDL Listed | 2 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 74.8 | 0.09023 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 82028.1997 | ng/dscm | 7.4754e-05 | ND, MDL listed | 3 | 1398
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 196 | 0.2454 | mg/Nm3 | Unknown | 2010-02-17 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 223079.3596 | ng/dscm | 0.00019638 | Blank = 0.0385 | 1 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 255 | 0.3287 | mg/Nm3 | Unknown | 2010-02-18 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 298833.3559 | ng/dscm | 0.00025455 | Blank = 0.0385 | 2 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 203 | 0.2637 | mg/Nm3 | Unknown | 2010-02-19 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 239739.6672 | ng/dscm | 0.00020258 | Blank = 0.0385 | 3 | 560
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 102 | 0.1465 | mg/Nm3 | Unknown | 2010-02-23 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 133167.591 | ng/dscm | 0.00010196 | 0.0385 (BLANK) | 1 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 167 | 0.2344 | mg/Nm3 | Unknown | 2010-02-25 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 213094.9191 | ng/dscm | 0.00016711 | 0.0385 (Blank) | 3 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 159 | 0.2228 | mg/Nm3 | Unknown | 2010-02-24 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 202574.3992 | ng/dscm | 0.00015861 | 0.0385 (Blank) | 2 | 565
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 56.7 | 0.0748 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A | [5 empty] | ND | BDL | 0 | ng/dscm | 5.67e-05 | G - Elevated reporting Limit due to matrix interference | 1 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 131 | 0.1724 | mg/Nm3 | Unknown | 2010-05-26 | Not Specified | EPA method 26A | [5 empty] | B, G | DLL | 156690.9256 | ng/dscm | 0.00013126 | B - estimated result, less than reporting limit G- elevated reporting limit due to matrix interference | 2 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Healy 6288_1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 25 |  | Golden Valley Electric Association | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 177 | 0.2293 | mg/Nm3 | Unknown | 2010-05-27 | Not Specified | EPA method 26A | [5 empty] | B, G | DLL | 208453.606 | ng/dscm | 0.00017683 | B - Estimated results is less than reporting limit G- elevated reporting limit due to matrix interference | 3 | 1257
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 1 |  | 138 | 0.1278 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 116180.7572 | ng/dscm | 0.00013842 |  | 1 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 2 |  | 134 | 0.1218 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 110699.382 | ng/dscm | 0.00013384 |  | 2 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 166 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 3 |  | 484 | 0.4407 | mg/Nm3 | Unknown | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 400596.9436 | ng/dscm | 0.00048364 |  | 3 | 863
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 1 |  | 236 | 0.2724 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 247643.8014 | ng/dscm | 0.00023567 |  | 1 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 2 |  | 282 | 0.3251 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 295574.5406 | ng/dscm | 0.00028242 |  | 2 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HMP&L Station Two Henderson 1382_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray,Natural) | Coal-Fired Boilers | 173 |  | Big Rivers Electric Corporation | bituminous | Interior(East, North) | KY | Wall-fired | Rear wall-fired boiler. | 3 |  | 397 | 0.4575 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A |  |  |  | Failing matrix spikes in lab data indicate matrix interference. |  | ADL | ADL | 415927.2751 | ng/dscm | 0.00039738 |  | 3 | 864
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 1 | < | 312 | 0.3722 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 338361.9386 | ng/dscm | 0.00031156 | [ | M26A-1 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 2 | < | 379 | 0.4532 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 412009.5423 | ng/dscm | 0.00037924 | [ | M26A-2 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Homer City Station 3122_HC3CONFIG | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 680 |  | Homer City OL1-OL8 LLC | bituminous | Eastern | PA | Wall-fired | Opposed wall-fired boiler. | 3 | < | 527 | 0.6338 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 576212.0826 | ng/dscm | 0.00052745 | [ | M26A-3 | 2015
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 | < | 679 | 0.816 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 741853.1626 | ng/dscm | 0.00067883 | [ | M23-2 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 695 | 0.8297 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 754257.6477 | ng/dscm | 0.00069515 | [ | M23-3 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 691 | 0.8306 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 755047.7249 | ng/dscm | 0.0006909 | [ | M23-1 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 | < | 68.8 | 0.09093 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 82666.1832 | ng/dscm | 6.8755e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 1 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 | < | 81.7 | 0.1058 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 96215.7054 | ng/dscm | 8.1674e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 2 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 | < | 69.7 | 0.08974 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81584.3127 | ng/dscm | 6.9671e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 3 | 1532
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 35.9 | 0.04579 | mg/Nm3 | Unknown | 2010-06-05 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 41626.957 | ng/dscm | 3.5885e-05 |  | 1 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 36.5 | 0.04568 | mg/Nm3 | Unknown | 2010-06-05 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 41525.5831 | ng/dscm | 3.6538e-05 |  | 2 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 34.9 | 0.0442 | mg/Nm3 | Unknown | 2010-06-06 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 40183.5924 | ng/dscm | 3.4876e-05 |  | 3 | 1336
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 | < | 66.7 | 0.08631 | mg/Nm3 | Unknown | 2010-05-10 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 78464.9484 | ng/dscm | 6.674e-05 |  | 1 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 95.9 | 0.1232 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 111967.0312 | ng/dscm | 9.5874e-05 |  | 2 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 | < | 66.1 | 0.0889 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 80817.4366 | ng/dscm | 6.6097e-05 |  | 3 | 1515
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 |  | 29200 | 39.13 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 35576759.4031 | ng/dscm | 0.029171 |  | 1 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 |  | 36300 | 48.39 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 43988026.0187 | ng/dscm | 0.036278 |  | 2 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 |  | 53700 | 71.16 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 64689627.9183 | ng/dscm | 0.053733 |  | 3 | 1348
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 |  | 35400 | 45.36 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 41237110.1708 | ng/dscm | 0.035429 |  | 1 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 |  | 46800 | 60.62 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 55106156.1138 | ng/dscm | 0.046778 |  | 2 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 |  | 41200 | 54.93 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 49935324.6266 | ng/dscm | 0.04121 |  | 3 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 1100 | 1.332 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 140180 | dscfm | 17.07 % moisture, 12.6 % CO2, 7.1 % O2, 315 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.8434 | ppmv | 0.0011 | [200] | 2 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 800 | 0.9624 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 143391 | dscfm | 15.65 % moisture, 12.7 % CO2, 7 % O2, 321 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.60919 | ppmv | 0.0008 | [200] | 3 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 600 | 0.7262 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | EPA method 26 | 148759 | dscfm | 14.1 % moisture, 12.7 % CO2, 7.1 % O2, 312 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.45963 | ppmv | 0.0006 | [200] | 1 | 213504
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 71300 | 93.45 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 84956472.6671 | ng/dscm | 0.07131 |  | M26A-1 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 71800 | 95.27 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 86610297.2563 | ng/dscm | 0.071754 |  | M26A-2 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 84500 | 112.2 | mg/Nm3 | Poor | 2010-05-26 | Not Specified | EPA method 26A |  |  |  | High results could not be explained by analytical or sampling error. No lab data available. Data flag not reported. |  |  | UNK | 101960289.0366 | ng/dscm | 0.084471 |  | M26A-3 | 128611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 149 | 0.1916 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 174192.6575 | ng/dscm | 0.00014916 |  | M26A-1 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 186 | 0.2385 | mg/Nm3 | Unknown | 2010-07-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 216775.0621 | ng/dscm | 0.00018562 |  | M26A-2 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 816 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 213 | 0.2724 | mg/Nm3 | Unknown | 2010-07-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 247597.7963 | ng/dscm | 0.00021344 |  | M26A-3 | 1286111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 327 | 0.3835 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 348647.248 | ng/dscm | 0.00032707 |  | M26A-1 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 254 | 0.3006 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 273266.6096 | ng/dscm | 0.00025449 |  | M26A-2 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | John E. Amos 3935_AM-3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 1300 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 356 | 0.4301 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 390967.4563 | ng/dscm | 0.0003563 |  | M26A-3 | 550005
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 480 | 0.7428 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 675243.7531 | ng/dscm | 0.0004802 |  | M5/29-1 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 540 | 0.8148 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 740714.8499 | ng/dscm | 0.00053951 |  | M5/29-2 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 604 | 0.9497 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 863405.492 | ng/dscm | 0.00060418 |  | M5/29-3 | 2009
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 602 | 0.7787 | mg/Nm3 | Unknown | 2010-07-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 707865.2315 | ng/dscm | 0.00060188 |  | M5/29-1 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 684 | 0.8964 | mg/Nm3 | Unknown | 2010-07-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 814924.0293 | ng/dscm | 0.00068428 |  | M5/29-2 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 637 | 0.8361 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 760078.051 | ng/dscm | 0.00063738 |  | M5/29-3 | 2097
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 665 | 0.8924 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 811266.5033 | ng/dscm | 0.0006649 | Lab J flag result between MDL and LOQ | 1 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 819 | 1.099 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 999260.3795 | ng/dscm | 0.00081861 | Lab J flag result between MDL and LOQ | 2 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 710 | 0.9462 | mg/Nm3 | Unknown | 2010-05-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 860211.3717 | ng/dscm | 0.00070962 | Lab J flag result between MDL and LOQ | 3 | 1372
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 1 | < | 16.1 | 0.01684 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 15305.017 | ng/dscm | 1.61e-05 |  | 1 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 2 | < | 14.6 | 0.02018 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 18349.9584 | ng/dscm | 1.4563e-05 |  | 2 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Logan Generating Plant 10043_Unit1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 242 |  | Logan Generating Company | bituminous | Eastern | WV | Wall-fired | Opposed wall-fired boiler. | 3 | < | 14.1 | 0.01966 | mg/Nm3 | Unknown | 2010-03-12 | Not Specified | EPA method 26A | [5 empty] | bdl | BDL | 17869.0681 | ng/dscm | 1.4098e-05 |  | 3 | 1266
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 206 | 0.2436 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221418.4774 | ng/dscm | 0.00020554 | 0.04 | 1 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 149 | 0.1763 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 160279.7501 | ng/dscm | 0.00014879 | 0.03 | 2 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 219 | 0.2592 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 235680.3502 | ng/dscm | 0.00021878 | 0.02 | 3 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 1 |  | 23900 | 30.78 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 27984307.6923 | ng/dscm | 0.02394 |  | 1 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 2 |  | 18300 | 23.95 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21775222.861 | ng/dscm | 0.018318 |  | 2 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marion Generating Station 976_123 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 120 |  | Southern Illinois Power Cooperative | bituminous | Interior(East, North) | IL | Fluidized bed |  | 3 |  | 20100 | 26.77 | mg/Nm3 | Unknown | 2010-06-11 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 24335792.0131 | ng/dscm | 0.020137 |  | 3 | 1430
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 283 | 0.3187 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 289731.2884 | ng/dscm | 0.00028283 | [ | 1 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 286 | 0.3221 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 292853.8115 | ng/dscm | 0.00028609 | [ | 2 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U12007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 289 | 0.3242 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 294712.8878 | ng/dscm | 0.00028879 | [ | 3 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 283 | 0.3187 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 289731.2884 | ng/dscm | 0.00028283 | [ | 1 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 286 | 0.3221 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 292853.8115 | ng/dscm | 0.00028609 | [ | 2 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U22007 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 400 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 289 | 0.3242 | mg/Nm3 | Unknown | 2010-08-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 294712.8878 | ng/dscm | 0.00028879 | [ | 3 | 2120
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 274 | 0.3026 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 275058.9798 | ng/dscm | 0.00027374 | [ | 1 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 311 | 0.3461 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 314676.2426 | ng/dscm | 0.00031147 | 392 ug | 2 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U3 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 394 | 0.438 | mg/Nm3 | Unknown | 2010-08-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 398214.8729 | ng/dscm | 0.00039385 | 480 ug | 3 | 2121
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 | < | 291 | 0.323 | mg/Nm3 | Unknown | 2010-08-24 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 293627.2298 | ng/dscm | 0.00029108 | [ | 1 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 | < | 276 | 0.3076 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 279632.0876 | ng/dscm | 0.00027635 | [ | 2 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Marshall 2727_U4 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 700 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 | < | 283 | 0.3161 | mg/Nm3 | Unknown | 2010-08-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 287334.6814 | ng/dscm | 0.00028287 | [ | 3 | 2122
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 434 | 0.5989 | mg/Nm3 | Unknown | 2010-03-30 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 544429.7426 | ng/dscm | 0.0004344 |  | M26A-1 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 518 | 0.7201 | mg/Nm3 | Unknown | 2010-03-31 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 654625.8382 | ng/dscm | 0.00051844 |  | M26A-2 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 505 | 0.6851 | mg/Nm3 | Unknown | 2010-04-01 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 622787.6557 | ng/dscm | 0.00050482 |  | M26A-3 | 698
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 1 |  | 498 | 0.6441 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 585582.7427 | ng/dscm | 0.00049837 | See laboratory report for additional information. | 1 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 759 | 0.9737 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 885188.1404 | ng/dscm | 0.00075851 | See laboratory report for additional information. | 2 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 990 | 1.279 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1162890.9435 | ng/dscm | 0.00098969 | See laboratory report for additional information. | 3 | 879456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 7600 | 10.89 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9898238.141 | ng/dscm | 0.0075985 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-1 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 7280 | 10.54 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9583149.111 | ng/dscm | 0.0072778 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-2 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 6950 | 10.06 | mg/Nm3 | Unknown | 2010-04-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9149592.2743 | ng/dscm | 0.0069485 | MDL established per 40CFR136B by standard deviation times " of replicate analyzes near instrument limit of detection. | M29-3 | 1654
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 7630 | 10.36 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 163426 | dscfm | 7.47 % moisture, 14.7 % CO2, 4.36 % O2, 414 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.56 | ppmv | 0.00763 | 26A | 1 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 7310 | 10.1 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 163351 | dscfm | 7.13 % moisture, 14.81 % CO2, 3.97 % O2, 417 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.39 | ppmv | 0.00731 | 26A | 2 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 6960 | 9.558 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 160792 | dscfm | 7.49 % moisture, 14.77 % CO2, 4.09 % O2, 417 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 6.05 | ppmv | 0.00696 | 26A | 3 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 261 | 0.3304 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 300351.4872 | ng/dscm | 0.00026068 |  | M26A-1 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 200 | 0.2537 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 230613.7512 | ng/dscm | 0.00020016 |  | M26A-2 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mountaineer 6264_Mt-1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox), SO3: SI | Coal-Fired Boilers | 1320 |  | Appalachian Power Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 | UNK | 181 | 0.2298 | mg/Nm3 | Poor | 2010-04-20 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 208896.3932 | ng/dscm | 0.00018131 |  | M26A-3 | 5500010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 1 |  | 344 | 0.4175 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 379535.0232 | ng/dscm | 0.00034367 |  | 1 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 2 |  | 571 | 0.6893 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 626658.448 | ng/dscm | 0.00057109 |  | 2 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 1&2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 553 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 3 |  | 345 | 0.4215 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 383188.8141 | ng/dscm | 0.00034526 |  | 3 | 1526
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 1 |  | 294 | 0.3617 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 328774.1669 | ng/dscm | 0.00029374 |  | 1 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 2 |  | 454 | 0.5617 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 510655.6766 | ng/dscm | 0.00045402 |  | 2 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mt. Storm 3954_Unit 3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 560 |  | Virginia Electric & Power Company | bituminous | Eastern | WV, MD, PA | Tangential |  | 3 |  | 107 | 0.1351 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A |  |  |  | Probe temperature not maintained |  | ADL | ADL | 122794.3455 | ng/dscm | 0.00010687 |  | 3 | 1527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 | < | 48.5 | 0.06235 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 56685.6849 | ng/dscm | 4.8538e-05 | [ | M26A-1 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 49.2 | 0.06488 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 58982.6659 | ng/dscm | 4.9185e-05 | [ | M26A-2 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 |  | 96.7 | 0.1267 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 115210.5184 | ng/dscm | 9.6705e-05 |  | M26A-3 | 1464
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 50 | 0.06084 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1806327 | dscfm | 15.6 % moisture, 12.8 % CO2, 5.9 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 56.7 | ppmv | 5e-05 | [200] | 1 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 50 | 0.06331 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1845061 | dscfm | 16.6 % moisture, 13.1 % CO2, 5.7 % O2, 116 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 59 | ppmv | 5e-05 | [200] | 2 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_001 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 |  | 100 | 0.1236 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | EPA method 26 | 1845641 | dscfm | 16.5 % moisture, 13.1 % CO2, 5.6 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. Emission factor conversion error | ADL | ADL | 115.2 | ppmv | 5e-05 | [200] | 3 | 1472
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 100 | 0.1298 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1844595 | dscfm | 15.7 % moisture, 13.4 % CO2, 6 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 121 | ppmv | 0.0001 | [200] | 1 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 50 | 0.06642 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1836298 | dscfm | 16.2 % moisture, 13.3 % CO2, 6 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<61.9] | ppmv | [<0.00005] | [200] | 2 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 50 | 0.06792 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | EPA method 26 | 1846014 | dscfm | 16.1 % moisture, 13.3 % CO2, 5.9 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<63.3] | ppmv | [<0.00005] | [200] | 3 | 1474
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 104 | 0.1331 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 120969.2611 | ng/dscm | 0.00010358 |  | M26A-1 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 | < | 52.6 | 0.06806 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 61873.7299 | ng/dscm | 5.2628e-05 | [ | M26A-2 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_002 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 52.7 | 0.06821 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 62005.7055 | ng/dscm | 5.274e-05 | [ | M26A-3 | 1465
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 106 | 0.1262 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [6 empty] | ADL | 114746.7309 | ng/dscm | 0.00010609 |  | M26A-1 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 118 | 0.1491 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [6 empty] | ADL | 135501.6796 | ng/dscm | 0.00011841 |  | M26A-2 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 57 | 0.07173 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | BDL | 65212.3741 | ng/dscm | 5.6987e-05 | [ | M26A-3 | 1467
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 1 |  | 110 | 0.1232 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1844402 | dscfm | 15.5 % moisture, 12.2 % CO2, 7 % O2, 116 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 114.8 | ppmv | 0.00011 | [200] | 1 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 2 |  | 120 | 0.1454 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1848466 | dscfm | 15.6 % moisture, 12.2 % CO2, 7.1 % O2, 115 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. Ug/m3 entered as ppmv. | ADL | ADL | 135.5 | ppmv | 0.00012 | [200] | 2 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Navajo Generating Station 4941_003 | NOx: Unspecified, PM: ESPh(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 812 |  | Salt River Project | bituminous | Rocky Mountain | San Juan (AZ) | Tangential |  | 3 | < | 60 | 0.06856 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | EPA method 26 | 1844770 | dscfm | 15.9 % moisture, 13.1 % CO2, 6.4 % O2, 117 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration data entry error. ug/m3 entered as ppmv. | BDL | BDL | [<63.9] | ppmv | [<.00006] | [200] | 3 | 1475
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 525 | 0.6495 | mg/Nm3 | Unknown | 2010-07-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 590420.8155 | ng/dscm | 0.00052522 | 690 (in units of ug) | 1 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 151 | 0.1881 | mg/Nm3 | Unknown | 2010-07-15 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 171016.3172 | ng/dscm | 0.00015058 | 200 (in units of ug; not detected with a reportable detection limit of 200 ug used as the final result) | 2 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 153 | 0.188 | mg/Nm3 | Unknown | 2010-07-16 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 170937.6891 | ng/dscm | 0.0001534 | 200 (in units of ug; not detected with a reportable detection limit of 200 ug used as the final result) | 3 | 1997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 128 | 0.1768 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 160686.5934 | ng/dscm | 0.00012786 |  | 1 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 167 | 0.231 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 209978.6876 | ng/dscm | 0.00016708 |  | 2 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 148 | 0.204 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 185434.9635 | ng/dscm | 0.00014755 |  | 3 | 1382
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 128 | 0.1675 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 220060 | dscfm | 18.2 % moisture, 14 % CO2, 4.8 % O2, 183 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.106 | ppmv | 0.000128 |  | 1 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 148 | 0.1927 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 221914 | dscfm | 17.6 % moisture, 15.1 % CO2, 4.8 % O2, 190 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.122 | ppmv | 0.000148 |  | 3 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Neil Simpson II 7504_NS2Cfg | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDcfb | Coal-Fired Boilers | 88 |  | Black Hills Power, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 167 | 0.2196 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | EPA method 26 | 224094 | dscfm | 18.1 % moisture, 15.1 % CO2, 4.8 % O2, 186 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.139 | ppmv | 0.000167 |  | 2 | 1384
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 625 | 0.8304 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 754931.2977 | ng/dscm | 0.00062496 |  | M5/29-1 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 388 | 0.5671 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 515584.321 | ng/dscm | 0.00038767 |  | M5/29-2 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 449 | 0.6485 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 589561.4205 | ng/dscm | 0.00044856 |  | M027/028-3 | 1902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 29900 | 36.58 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 33254468.4211 | ng/dscm | 0.029871 |  | 1 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 25500 | 31.68 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 28802686.2808 | ng/dscm | 0.025493 |  | 2 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 23600 | 29.39 | mg/Nm3 | Unknown | 2010-03-24 | Not Specified | EPA method 26A |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 26717350.3233 | ng/dscm | 0.023576 |  | 3 | 5000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 1 | < | 94.3 | 0.1186 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 107814.722 | ng/dscm | 9.434e-05 | [ | 1 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 184 | 0.2575 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 234133.1103 | ng/dscm | 0.00018364 | First section undetected, second section detected. See report for additional information. | 2 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 3 | < | 82.8 | 0.1161 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 105569.3412 | ng/dscm | 8.28e-05 | [ | 3 | 2025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 11700 | 13.57 | mg/Nm3 | Unknown | 2010-07-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12340715.8947 | ng/dscm | 0.011661 |  | 1 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 11700 | 13.44 | mg/Nm3 | Unknown | 2010-07-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12222348.8796 | ng/dscm | 0.01165 |  | 2 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 12100 | 14.08 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12801927.5089 | ng/dscm | 0.012121 |  | 3 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 11700 | 13.57 | mg/Nm3 | Unknown | 2010-07-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12340715.8947 | ng/dscm | 0.011661 |  | 1 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 11700 | 13.44 | mg/Nm3 | Unknown | 2010-07-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12222348.8796 | ng/dscm | 0.01165 |  | 2 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 12100 | 14.08 | mg/Nm3 | Unknown | 2010-07-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12801927.5089 | ng/dscm | 0.012121 |  | 3 | 2090
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 136 | 0.1901 | mg/Nm3 | Unknown | 2010-06-01 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 172863.5959 | ng/dscm | 0.00013622 |  | 1 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 39200 | 55.97 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 50882374.1266 | ng/dscm | 0.039157 |  | 2 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 41300 | 56.95 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26 |  |  |  |  | Missing data flag identified in lab report. |  | ADL | 51769879.0766 | ng/dscm | 0.041348 |  | 3 | 2088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 101 | 0.1338 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 121614.0024 | ng/dscm | 0.00010051 | See test report regarding detection limit information | M26A-1 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 80 | 0.1064 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 96739.9396 | ng/dscm | 7.9955e-05 | See test report regarding detection limit information | M26A-2 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 655 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 109 | 0.1425 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 129566.2511 | ng/dscm | 0.0001092 | See test report regarding detection limit information | M26A-3 | 732001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 97.4 | 0.1271 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 115539.6519 | ng/dscm | 9.7378e-05 | See test report regarding detection limit information | M26A-1 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 104 | 0.1325 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 120419.5552 | ng/dscm | 0.00010423 | See test report regarding detection limit information | M26A-2 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pleasant Prairie 6170_PPPPB2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 643 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 81.7 | 0.1038 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 94352.469 | ng/dscm | 8.167e-05 | See test report regarding detection limit information | M26A-3 | 733
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 | < | 410 | 0.5363 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 487590.0027 | ng/dscm | 0.00041008 | [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 | < | 411 | 0.5395 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 490482.3055 | ng/dscm | 0.00041143 | [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 4 | < | 373 | 0.4967 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 451574.1809 | ng/dscm | 0.00037291 | [ | M26A-4 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 | < | 410 | 0.5363 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 487590.0027 | ng/dscm | 0.00041008 | [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 | < | 411 | 0.5395 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 490482.3055 | ng/dscm | 0.00041143 | [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 4 | < | 373 | 0.4967 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 451574.1809 | ng/dscm | 0.00037291 | [ | M26A-4 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 | < | 309 | 0.3591 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 326465.6484 | ng/dscm | 0.00030853 | [ | M29-3 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 | < | 285 | 0.3362 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 305643.4514 | ng/dscm | 0.00028464 | [ | M26A-4 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 5 | < | 311 | 0.3624 | mg/Nm3 | Unknown | 2010-03-18 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 329429.0412 | ng/dscm | 0.00031133 | [ | M26A-5 | 1185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 | < | 407 | 0.4846 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 440553.2904 | ng/dscm | 0.0004073 | [ | M26A-4 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 5 | < | 327 | 0.3839 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 349016.0764 | ng/dscm | 0.00032742 | [ | M26A-5 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 6 | < | 335 | 0.3927 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 26A |  |  |  | Results uncertain due to high blank values possibly indicating contamination |  | BDL | BDL | 356991.7168 | ng/dscm | 0.0003349 | [ | M26A-6 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 1 |  | 1320 | 1.738 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 320 |  |  | 10.7 % moisture, 13.4 % CO2, 6.21 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00073766 | ppmv | 0.00132 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 1 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 2 |  | 1340 | 1.793 | mg/Nm3 | Unknown | 2010-04-10 | Refer to sample method | U.S. EPA Method 320 |  |  | 11.4 % moisture, 13.6 % CO2, 5.95 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00076113 | ppmv | 0.00134 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 2 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 3 |  | 886 | 1.153 | mg/Nm3 | Unknown | 2010-04-10 | Refer to sample method | U.S. EPA Method 320 |  |  | 11.6 % moisture, 13.7 % CO2, 5.84 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 0.00048954 | ppmv | 0.000886 | The measured value is actually ppmdv as measured by the instrument for Method 320 | 3 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 7090 | 9.111 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 8282978.3076 | ng/dscm | 0.007094 | 30000, Blank ND | 1 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 7540 | 10.2 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 9271130.7957 | ng/dscm | 0.0075436 | 33900, Blank ND | 2 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 8990 | 12.24 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 11129503.4382 | ng/dscm | 0.0089886 | 40600, Blank ND | 3 | 2302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 503 | 0.6373 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 579329.4881 | ng/dscm | 0.00050266 |  | 2 | 947
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 164 | 0.21 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 190880.7752 | ng/dscm | 0.00016442 |  | 3 | 947
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 415 | 2.039 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 19.2 % moisture, 13.4 % CO2, 5 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1900 | ppmv | 0.00041455 |  | 1 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 444 | 2.146 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.7 % moisture, 13.8 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 2000 | ppmv | 0.00044428 |  | 2 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 241 | 1.18 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.9 % moisture, 14.1 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1100 | ppmv | 0.00024144 |  | 3 | 1043
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 415 | 2.039 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 19.2 % moisture, 13.4 % CO2, 5 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1900 | ppmv | 0.00041455 |  | 1 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 444 | 2.146 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.7 % moisture, 13.8 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 2000 | ppmv | 0.00044428 |  | 2 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 241 | 1.18 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | EPA method 26 |  |  | 18.9 % moisture, 14.1 % CO2, 5.3 % O2 |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error from lb/mmbtu to ppm | ADL | ADL | 1100 | ppmv | 0.00024144 |  | 3 | 1044
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 1 |  | 5450 | 5.941 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5401093.6698 | ng/dscm | 0.0054461 |  | M29-1 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 2 |  | 5420 | 5.696 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 5178473.7733 | ng/dscm | 0.0054242 |  | M29-2 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 3 |  | 6270 | 7.239 | mg/Nm3 | Unknown | 2010-05-08 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 6580977.1679 | ng/dscm | 0.0062688 |  | M29-3 | 1972
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 1 |  | 8020 | 8.769 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7971515.8472 | ng/dscm | 0.0080157 | HF 34800, Blank N/D | 1 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 2 |  | 7680 | 8.784 | mg/Nm3 | Unknown | 2010-06-15 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7985665.9718 | ng/dscm | 0.0076803 | HF 15900, Blank N/D | 2 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 3 |  | 7620 | 8.228 | mg/Nm3 | Unknown | 2010-06-16 | Not Specified | EPA method 26A |  |  |  |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 7479871.7767 | ng/dscm | 0.007617 | HF 32900, Blank N/D | 3 | 1906
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 71700 | 86 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78183310.5066 | ng/dscm | 0.071711 | 80900+234 ug | 7A-1 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 72000 | 86.65 | mg/Nm3 | Unknown | 2010-04-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78773739.6212 | ng/dscm | 0.071994 | 81900+ 295 ug | 7A-2 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 73400 | 88.33 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 80295953.134 | ng/dscm | 0.073438 | 82400+258 ug | 7A-3 | 902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 70900 | 87.1 | mg/Nm3 | Unknown | 2010-04-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 79181280.654 | ng/dscm | 0.070943 | 82000+ 275 ug | 7B-1 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 72700 | 88.95 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 80860145.7726 | ng/dscm | 0.072652 | 81400+266 ug | 7B-3 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 70800 | 86.82 | mg/Nm3 | Unknown | 2010-04-12 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 78926282.5842 | ng/dscm | 0.070814 | 80900+281 ug | 7B-2 | 903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 35.7 | 0.04313 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 39209.648 | ng/dscm | 3.5682e-05 |  | M23-1 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 78.3 | 0.09626 | mg/Nm3 | Unknown | 2010-06-19 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 87504.7291 | ng/dscm | 7.8291e-05 |  | M23-2 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 105 | 0.1299 | mg/Nm3 | Unknown | 2010-06-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 118078.889 | ng/dscm | 0.0001055 |  | M23-3 | 2022
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 | < | 25 | 0.03012 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 27378.0615 | ng/dscm | 2.4968e-05 |  | M29-1 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 16.9 | 0.02017 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 18334.6557 | ng/dscm | 1.6902e-05 |  | M29-2 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 54.7 | 0.06545 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 59501.6647 | ng/dscm | 5.4655e-05 |  | M29-3 | 2021
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4980 | 6.509 | mg/Nm3 | Poor | 2010-07-13 | Refer to sample method | U.S. EPA Method 26A-Mod | 1328719 | dscfm | 13.53 % moisture, 14.24 % CO2, 4.92 % O2, 331 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 4.12 | ppmv | 0.00498 | Modified Method 26 - non isokinetic | 1 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1360 | 1.754 | mg/Nm3 | Poor | 2010-07-14 | Refer to sample method | U.S. EPA Method 26A-Mod | 1333580 | dscfm | 14.11 % moisture, 14.09 % CO2, 5.12 % O2, 331 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 1.11 | ppmv | 0.00136 | Modified Method 26 - non isokinetic | 2 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1400 | 1.864 | mg/Nm3 | Poor | 2010-07-15 | Refer to sample method | U.S. EPA Method 26A-Mod | 1359968 | dscfm | 12.55 % moisture, 15.1 % CO2, 4.61 % O2, 326 deg F | Samples collected in combined train against EPA guidance. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 1.18 | ppmv | 0.0014 | Modified Method 26 - non isokinetic | 3 | 2100
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 1380 | 1.732 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1574646.2493 | ng/dscm | 0.001376 |  | 2 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 2630 | 3.339 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 3035071.3662 | ng/dscm | 0.0026342 |  | 3 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 4 |  | 2110 | 2.509 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 2280652.3834 | ng/dscm | 0.0021085 |  | 4 | 2161
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 | < | 121 | 0.1519 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 138086.0105 | ng/dscm | 0.00012067 | Analysis for HCl was non-detect with detection limit substituted | 1 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 | < | 120 | 0.151 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 137304.5832 | ng/dscm | 0.00011999 | Analysis for HCl was non-detect with detection limit substituted | 2 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 | < | 93.4 | 0.1176 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 106884.0297 | ng/dscm | 9.3403e-05 | Analysis for HCl was non-detect with detection limit substituted | 3 | 2315
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 | < | 112 | 0.1419 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 129040.0681 | ng/dscm | 0.000112 | Analysis for HCl was non-detect with detection limit substituted | 1 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 | < | 99.2 | 0.1249 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 113505.1439 | ng/dscm | 9.9189e-05 | Analysis for HCl was non-detect with detection limit substituted | 2 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 | < | 161 | 0.2026 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 184226.7032 | ng/dscm | 0.00016099 | Analysis for HCl was non-detect with detection limit substituted | 3 | 23151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 | < | 64.2 | 0.08579 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 77989.0837 | ng/dscm | 6.4195e-05 |  | 1 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 | < | 121 | 0.1604 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 145791.6462 | ng/dscm | 0.00012078 |  | 2 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 | < | 103 | 0.1385 | mg/Nm3 | Unknown | 2010-07-01 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 125886.9182 | ng/dscm | 0.00010296 |  | 3 | 23152
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 | < | 117 | 0.1552 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 141085.2713 | ng/dscm | 0.00011689 | Analysis for HCl was non-detect with detection limit substituted | 2 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 | < | 114 | 0.1511 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 137376.7862 | ng/dscm | 0.00011381 | Analysis for HCl was non-detect with detection limit substituted | 3 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 | < | 123 | 0.1609 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 146253.2535 | ng/dscm | 0.00012276 | Analysis for HCl was non-detect with detection limit substituted | 1 | 23153
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 | < | 100 | 0.1478 | mg/Nm3 | Unknown | 2010-03-03 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 134359.9522 | ng/dscm | 0.00010048 | Non-Detect, Reported as Laboratory Detection Limit | 1 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 | < | 100 | 0.1468 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 133426.2899 | ng/dscm | 0.00010037 | Non-Detect, Reported as Laboratory Detection Limit; Temperature dipped slightly below 248 degF for approximately 30 minutes, which can cause a low bias in measurement. Samples were collected in combined train with HCN, which is contrary to more recent EPA | 2 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 | < | 76.5 | 0.1125 | mg/Nm3 | Unknown | 2010-03-05 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 102243.1018 | ng/dscm | 7.6461e-05 | Non-Detect, Reported as Laboratory Detection Limit | 3 | 834
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 | < | 30 | 0.0452 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 41094.0785 | ng/dscm | 3.0033e-05 | Non-Detect, Reported as Laboratory Detection Limit; Temperature briefly dipped below 248 degF, which can cause a low bias in measurement. Samples were collected in combined train with HCN, which is contrary to more recent EPA recommendations posted on ICR | 1 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 | < | 29.8 | 0.04493 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 40843.0045 | ng/dscm | 2.985e-05 | Non-Detect, Reported as Laboratory Detection Limit | 2 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 | < | 30.7 | 0.0459 | mg/Nm3 | Unknown | 2010-03-11 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 41727.2987 | ng/dscm | 3.067e-05 | Non-Detect, Reported as Laboratory Detection Limit | 3 | 830
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 101000 | 119.5 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 108668890.2645 | ng/dscm | 0.1012 |  | 1 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 109000 | 129.6 | mg/Nm3 | Unknown | 2010-03-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 117849397.1335 | ng/dscm | 0.10896 |  | 2 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 115000 | 136.7 | mg/Nm3 | Unknown | 2010-03-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 124260459.1164 | ng/dscm | 0.11488 |  | 3 | 2179
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 | < | 74700 | 100.7 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 91504745.7547 | ng/dscm | 0.074696 |  | 1 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 | < | 74000 | 99 | mg/Nm3 | Unknown | 2010-03-22 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 90002123.4929 | ng/dscm | 0.074006 |  | 2 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 | < | 81400 | 105.9 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A |  |  |  | High DLs due to combined M26/HCH train. | Missing data flag identified in lab report. |  | BDL | 96251284.8708 | ng/dscm | 0.081444 |  | 3 | 10000000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 | < | 161 | 0.2091 | mg/Nm3 | Unknown | 2010-04-13 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 190080.6027 | ng/dscm | 0.00016075 | BDL [<150] | 1 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 157 | 0.2055 | mg/Nm3 | Unknown | 2010-04-14 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 186814.9744 | ng/dscm | 0.00015732 | ADL 276, ADL 161 | 2 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 124 | 0.1613 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A | [5 empty] | DLL | DLL | 146617.3797 | ng/dscm | 0.00012419 | ADL 167, BDL [<180] | 3 | 524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 88200 | 91.98 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83622017.2061 | ng/dscm | 0.088164 | Impinger Solution 253000, DI Water 7780, Blank 716 | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 88200 | 93.09 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84629159.4416 | ng/dscm | 0.088159 | Impinger Solution 255000, DI Water 6600, Blank 716 | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 91600 | 94.29 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 85720075.0986 | ng/dscm | 0.091594 | Impinger Solution 256000, DI Water 12300, Blank 716 | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 88200 | 91.98 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 83622017.2061 | ng/dscm | 0.088164 | Impinger Solution 253000, DI Water 7780, Blank 716 | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 88200 | 93.09 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84629159.4416 | ng/dscm | 0.088159 | Impinger Solution 255000, DI Water 6600, Blank 716 | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 91600 | 94.29 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 85720075.0986 | ng/dscm | 0.091594 | Impinger Solution 256000, DI Water 12300, Blank 716 | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 1830 | 2.101 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | EPA method 26 | 164477 | dscfm | 10.92 % moisture, 10.5 % CO2, 9.3 % O2, 318 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0018339 |  | 1 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 1570 | 1.801 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | EPA method 26 | 166539 | dscfm | 8.78 % moisture, 10.5 % CO2, 9.5 % O2, 323 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0015704 |  | 2 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 1590 | 1.817 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | EPA method 26 | 168741 | dscfm | 8.73 % moisture, 10.5 % CO2, 9.5 % O2, 324 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Concentration missing | ADL | ADL |  | ppmv | 0.0015856 |  | 3 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 1 |  | 15600 | 21.2 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19273147.649 | ng/dscm | 0.015618 |  | M5/29-1 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 2 |  | 15500 | 21.19 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19266275.372 | ng/dscm | 0.015469 |  | M5/29-2 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 3 |  | 17000 | 23.43 | mg/Nm3 | Unknown | 2010-05-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21300162.8283 | ng/dscm | 0.017016 |  | M5/29-3 | 1915
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 | < | 72.5 | 0.08923 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 81121.9236 | ng/dscm | 7.2478e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 1 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 | < | 78 | 0.09566 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 86966.4477 | ng/dscm | 7.7973e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 2 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 | < | 82.4 | 0.1024 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 93119.4488 | ng/dscm | 8.2447e-05 | Detection level is determined by calibrating to the minimum level required by the method and using the average area count obtained for the lowest calibration standard. If the lowest calibration standard utilized is higher than that typically specified in | 3 | 1524
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 30.6 | 0.0346 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 322 | 834323 | dscfm | 200.5 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.0219 | ppmv | 3.0566e-05 | 0.602,[<0.02],0.021,DLL | Sample 3 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 29.5 | 0.03349 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 321 | 829503 | dscfm | 200.9 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.0212 | ppmv | 2.9482e-05 | 0.602,[<0.02],0.021,DLL | Sample 2 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 858 | 0.9726 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 320 | 829805 | dscfm | 201.2 deg F | Wet basis concentrations indicated but values could not be converted to dry basis because flue gas moisture was not provided. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | DLL | DLL | 0.6156 | ppmv | 0.00085788 | 0.602,[<0.02],0.021,DLL | Sample 1 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 6580 | 8.856 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 320 | 834669 | dscfm | 15.6 % moisture, 195.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 4.72 | ppmv | 0.00658 | 4.7734,5.3198,[<0.02],DLL | Sample 1 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 7330 | 9.846 | mg/Nm3 | Unknown | 2010-05-09 | Refer to sample method | U.S. EPA Method 321 | 847024 | dscfm | 15.6 % moisture, 195 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 5.26 | ppmv | 0.00733 | 4.7734,5.3198,[<0.02],DLL | Sample 2 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 28.5 | 0.03828 | mg/Nm3 | Unknown | 2010-05-09 | Refer to sample method | U.S. EPA Method 322 | 832041 | dscfm | 15.8 % moisture, 192.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Wet basis ppm concentration values indicated. Converted to dry basis using the reported flue gas moisture. | DLL | DLL | 0.0205 | ppmv | 2.85e-05 | 4.7734,5.3198,[<0.02],DLL | Sample 3 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 | UNK | 1440 | 1.998 | mg/Nm3 | Poor | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1816008.4463 | ng/dscm | 0.00144 |  | 1 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | UNK | 1500 | 2.047 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 1861060.3484 | ng/dscm | 0.0014952 |  | 2 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN1 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | UNK | 2390 | 3.428 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 3116094.8239 | ng/dscm | 0.0023878 |  | 3 | 1346
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 16 | 0.02313 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 21031.3207 | ng/dscm | 1.5953e-05 |  | 1 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 18.3 | 0.02608 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 23709.6707 | ng/dscm | 1.8267e-05 |  | 2 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | < | 16.6 | 0.0228 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 20726.4832 | ng/dscm | 1.6579e-05 |  | 3 | 13461
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 29.9 | 0.04293 | mg/Nm3 | Unknown | 2010-04-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 39028.2878 | ng/dscm | 2.9888e-05 |  | 1 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 9.39 | 0.01361 | mg/Nm3 | Unknown | 2010-04-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 12374.746 | ng/dscm | 9.3866e-06 |  | 2 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN3 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 | < | 9.08 | 0.01324 | mg/Nm3 | Unknown | 2010-04-19 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 12038.4809 | ng/dscm | 9.0776e-06 |  | 3 | 134611
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 | < | 13.6 | 0.0192 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 17454.0423 | ng/dscm | 1.3578e-05 |  | 1 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 | < | 13.4 | 0.01962 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 17836.1318 | ng/dscm | 1.3418e-05 |  | 2 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN4 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 |  | 88.3 | 0.1107 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 100659.2822 | ng/dscm | 8.8265e-05 |  | 3 | 1346111
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1550 | 1.916 | mg/Nm3 | Unknown | 2010-06-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1741920.5106 | ng/dscm | 0.0015541 |  | 1 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 869 | 1.071 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 973935.8584 | ng/dscm | 0.00086895 |  | 2 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 725 | 0.838 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 761829.6765 | ng/dscm | 0.00072536 |  | 3 | 2081
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 51000 | 57.03 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 368595 | dscfm | 7.4 % moisture, 10.5 % CO2, 8.2 % O2, 285.3 deg F | The data was corrected by the sample contractor for sample line bias due to known off-gassing of formaldehyde from heated sample lines. One-half the average system zero concentration accounted for 30 to 50% of the uncorrected test run results. | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.051 |  | 1 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 52000 | 63.35 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 367737 | dscfm | 7.2 % moisture, 10.4 % CO2, 8.3 % O2, 287.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.052 |  | 2 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 52000 | 63.35 | mg/Nm3 | Unknown | 2010-08-13 | Refer to sample method | U.S. EPA Method 320 | 368102 | dscfm | 7.3 % moisture, 10.3 % CO2, 8.4 % O2, 288.9 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. Conversion error | ADL | ADL | 32.7 | ppmv | 0.052 |  | 3 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 15500 | 19.69 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 17899885.077 | ng/dscm | 0.015493 |  | 1 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 15700 | 21.15 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 19228238.5998 | ng/dscm | 0.015742 |  | 2 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 16800 | 22.36 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 20322891.376 | ng/dscm | 0.016843 |  | 3 | 1942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 1 | UNK | 17900 | 24.65 | mg/Nm3 | Poor | 2010-05-25 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 22410958.3928 | ng/dscm | 0.017871 |  | M29-1 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 | UNK | 16700 | 23.18 | mg/Nm3 | Poor | 2010-05-26 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 21073161.1894 | ng/dscm | 0.016699 |  | M29-2 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 3 | UNK | 19000 | 25.59 | mg/Nm3 | Poor | 2010-05-28 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 23261147.4838 | ng/dscm | 0.019024 |  | M29-3 | 12861
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | < | 65 | 0.08238 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 74888.8964 | ng/dscm | 6.4998e-05 | Sample Below Detection Limit | 1 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | < | 65 | 0.08008 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 72800.1253 | ng/dscm | 6.4952e-05 | Lower Reportable limit from lab 250 ug | 2 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 65.5 | 0.08354 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 75941.9642 | ng/dscm | 6.5467e-05 | Lab reporting limit 250 ug | 3 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 1 |  | 563 | 0.6493 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | EPA method 26 | 245541 | dscfm | 6.8 % O2, 294.3 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.411 | ppmv | 0.000563 |  | 1 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 2 |  | 776 | 0.8942 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | EPA method 26 | 245758 | dscfm | 6.8 % O2, 297.1 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.566 | ppmv | 0.000776 |  | 2 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 3 |  | 578 | 0.6604 | mg/Nm3 | Unknown | 2010-07-21 | Refer to sample method | EPA method 26 | 246190 | dscfm | 6.9 % O2, 290 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | ADL | ADL | 0.418 | ppmv | 0.000578 |  | 3 | 1456
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 214 | 0.2574 | mg/Nm3 | Unknown | 2010-03-03 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 234016.1319 | ng/dscm | 0.00021416 | 1.39ug/ml, 0.266ug/ml (Blank), 665ml sample volume - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven | 2 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 211 | 0.2569 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 233557.4938 | ng/dscm | 0.00021118 | 1.39ug/ml, 0.266ug/ml (Blank), 690 ml sample vol. - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven | 3 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valmont 477_Unit 5 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 196 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 4 |  | 208 | 0.2551 | mg/Nm3 | Unknown | 2010-03-04 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 231913.0116 | ng/dscm | 0.00020798 | 1.34ug/ml, 0.266ug/ml (Blank), 700 ml sample - Method Detection Limit for HCl and HF was determined using procedures outlined in 40 CFR Part 136 App B "Definition and Procedures for the Determination of the Method Detection Limit - Rev 1.11" Seven injec | 4 | 1460
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 923 | 1.121 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1019294.7871 | ng/dscm | 0.00092297 | 2840 ug | 1 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 802 | 0.9759 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 887163.122 | ng/dscm | 0.00080162 | 2440 ug | 2 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 909 | 1.107 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1006644.615 | ng/dscm | 0.00090894 | 2740 ug | 3 | 908
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 91000 | 92.69 | mg/Nm3 | Unknown | 2010-02-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84265364.4925 | ng/dscm | 0.090953 | 342 | 1 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 99700 | 98.87 | mg/Nm3 | Unknown | 2010-02-16 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 89884370.2732 | ng/dscm | 0.09967 | 355 | 2 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 98800 | 93.04 | mg/Nm3 | Unknown | 2010-02-17 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 84585615.395 | ng/dscm | 0.098833 | 338 | 3 | 979
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 1 |  | 13400 | 15.76 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14329683.1043 | ng/dscm | 0.013423 |  | 1 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 2 |  | 12700 | 14.95 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 13586692.8606 | ng/dscm | 0.012709 |  | 2 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 3 |  | 11900 | 13.94 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12669026.5903 | ng/dscm | 0.011894 |  | 3 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 13400 | 15.76 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 14329683.1043 | ng/dscm | 0.013423 |  | 1 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 12700 | 14.95 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 13586692.8606 | ng/dscm | 0.012709 |  | 2 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 11900 | 13.94 | mg/Nm3 | Unknown | 2010-06-10 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 12669026.5903 | ng/dscm | 0.011894 |  | 3 | 1636
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 160 | 0.2005 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 182282.1444 | ng/dscm | 0.00015994 | 0.209 | 1 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 | < | 30.7 | 0.03829 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 34804.8877 | ng/dscm | 3.075e-05 | [<.04] | 2 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 | < | 30.5 | 0.03821 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 26A | [5 empty] | BDL | BDL | 34735.574 | ng/dscm | 3.0478e-05 | [<0.02] | 3 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 1 |  | 242 | 0.2607 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 236972.3123 | ng/dscm | 0.00024187 |  | 1 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 2 |  | 458 | 0.5523 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 502096.5136 | ng/dscm | 0.00045757 |  | 2 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 1 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 3 |  | 233 | 0.291 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 264541.4348 | ng/dscm | 0.00023277 |  | 3 | 1980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 1 |  | 237 | 0.301 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 273606.3924 | ng/dscm | 0.00023747 |  | 1 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 2 |  | 208 | 0.2598 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 236155.4534 | ng/dscm | 0.00020779 |  | 2 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wansley 6052_Unit 2 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 920 |  | Georgia Power | bituminous | Interior(East, North), Eastern | IL, IN, KY, TN, WV | Tangential |  | 3 |  | 216 | 0.2424 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 220388.5954 | ng/dscm | 0.00021629 |  | 3 | 19801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1800 | 2.013 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 1830299.2069 | ng/dscm | 0.0017991 |  | M23-1 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 560 | 0.653 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 593609.1077 | ng/dscm | 0.00056004 |  | M23-2 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 464 | 0.5266 | mg/Nm3 | Unknown | 2010-07-22 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 478731.971 | ng/dscm | 0.00046372 |  | M23-3 | 2013
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 | UNK | 171 | 0.209 | mg/Nm3 | Poor | 2010-04-13 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 190019.2365 | ng/dscm | 0.00017073 |  | M29-1 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 | UNK | 216 | 0.2551 | mg/Nm3 | Poor | 2010-04-14 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 231880.8252 | ng/dscm | 0.00021595 |  | M29-2 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 | < | 197 | 0.2399 | mg/Nm3 | Unknown | 2010-04-15 | Not Specified | EPA method 26A |  |  |  | No lab data available. Data flag not reported. |  |  | BDL | 218115.7497 | ng/dscm | 0.00019667 |  | M29-3 | 10040004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 63.2 | 0.07872 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 71565.2608 | ng/dscm | 6.318e-05 | The value is not blank corrected as the blank value was BDL. | 1 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 231 | 0.2877 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 261577.1267 | ng/dscm | 0.00023093 | The value is not blank corrected as the blank value was BDL. | 2 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 193 | 0.2432 | mg/Nm3 | Unknown | 2010-03-23 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 221070.9363 | ng/dscm | 0.0001931 | The value is not blank corrected as the blank value was BDL. | 3 | 3197
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 5300 | 6.742 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 6129269.945 | ng/dscm | 0.0053045 | HCl 18700, Blank 0.0 | 1 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 8830 | 11.17 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 10150640.6418 | ng/dscm | 0.0088334 | HCl 31200, Blank 0.0 | 2 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whitewater Valley 1040_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 69 |  | City of Richmond | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 7650 | 9.632 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 26A |  |  |  |  | Missing flag assigned based on ERT comment field entry. | 0 | ADL | 8756238.2107 | ng/dscm | 0.0076487 | HCl 27600, Blank 0.0 | 3 | 2038
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 179 | 0.2629 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 239007.5188 | ng/dscm | 0.00017906 |  | 1 | 1488
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 134 | 0.1981 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 180058.3702 | ng/dscm | 0.00013411 |  | 2 | 1488
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 128 | 0.1801 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | EPA method 26 | 223 | dscfm | 17.3 % moisture, 15.7 % CO2, 3.7 % O2, 186 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.114 | ppmv | 0.000128 |  | 2 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 179 | 0.2496 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | EPA method 26 | 238050 | dscfm | 15.1 % moisture, 15.5 % CO2, 3.8 % O2, 184 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.158 | ppmv | 0.000179 |  | 1 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 471 | 0.632 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | EPA method 26 | 248616 | dscfm | 15.1 % moisture, 15.3 % CO2, 4.4 % O2, 182 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.4 | ppmv | 0.000471 |  | 1 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 353 | 0.474 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | EPA method 26 | 240230 | dscfm | 16.5 % moisture, 14.4 % CO2, 4.4 % O2, 180 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.3 | ppmv | 0.000353 |  | 2 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 353 | 0.474 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | EPA method 26 | 227964 | dscfm | 17.1 % moisture, 15 % CO2, 4.4 % O2, 180 deg F |  | Concentration reported as ppmv in ICR database was converted to ug/m3 for the PPTMD database using MW. | BDL | BDL | 0.3 | ppmv | 0.000353 |  | 3 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 | < | 461 | 0.6532 | mg/Nm3 | Unknown | 2010-05-04 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 593774.4035 | ng/dscm | 0.00046101 |  | 1 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 | < | 376 | 0.5235 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 475882.5115 | ng/dscm | 0.00037632 |  | 3 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 | < | 363 | 0.5138 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 26 | [5 empty] | ND | BDL | 467120.108 | ng/dscm | 0.00036267 |  | 2 | 1156
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 1 |  | 203 | 0.2101 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 190971.3188 | ng/dscm | 0.00020304 |  | 1 | 1978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 2 |  | 157 | 0.1695 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 154051.96 | ng/dscm | 0.00015724 |  | 2 | 1978
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Yates 728_Y1BR | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 107 |  | Georgia Power | bituminous | Eastern | KY, TN, VA, WV | Tangential |  | 3 |  | 129 | 0.1278 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 26A | [5 empty] | ADL | ADL | 116187.4495 | ng/dscm | 0.0001289 |  | 3 | 1978