## raw
EPRI Power Plant Toxics Measurement Database
2017-02-27 17:55
Copyright 2015 Electric Power Research Institute (EPRI), Inc. All rights reserved.
Electric Power Research Institute and EPRI are registered service marks of the Electric Power Research Institute, Inc. EPRI.
Stack Emissions Data
Data Sources: 2010 Utility HAPs Information Collection Request
Selected chemical substances: Mercury
Coal Type: All
Selected Chemical: Mercury
USGS Province: All
Boiler Type: All
Gas-Side Controls: All Controls
Data Quality: Include All
Non-Detect Data: Use detection limit
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments | Changes to Reported ICR Data | ICR Reported Data Flag | ICR Standardized Data Flag | ICR Reported Concentration | ICR Reported Units of Measure | ICR Emission Factor (lb/million Btu) | ICR Reported Data Comments | ICR Reported Run Number | ICR Submittal ID
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.299 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 603270 | dscfm | 14 %H20, 12.2 %CO2, 6.4 %O2, 127.6 Deg F |  |  | ADL | ADL | 0.34 | ug/dscm | 2.9924e-07 |  | 1A | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.305 | 0.0003755 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 604361 | dscfm | 14 %H20, 12.3 %CO2, 6.4 %O2, 127.6 Deg F |  |  | ADL | ADL | 0.35 | ug/dscm | 3.0536e-07 |  | 2A | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.306 | 0.0003755 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 610789 | dscfm | 14.6 %H20, 12.3 %CO2, 6.2 %O2, 127.9 Deg F |  |  | ADL | ADL | 0.35 | ug/dscm | 3.0598e-07 |  | 3A | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.301 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 603270 | dscfm | 14 %H20, 12.2 %CO2, 6.4 %O2, 127.6 Deg F |  |  | ADL | ADL | 0.34 | ug/dscm | 3.0057e-07 |  | 1B | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.324 | 0.000397 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 604361 | dscfm | 14 %H20, 12.3 %CO2, 6.4 %O2, 127.6 Deg F |  |  | ADL | ADL | 0.37 | ug/dscm | 3.2424e-07 |  | 2B | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.295 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 610789 | dscfm | 14.6 %H20, 12.3 %CO2, 6.2 %O2, 127.9 Deg F |  |  | ADL | ADL | 0.34 | ug/dscm | 2.9509e-07 |  | 3B | 541
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 | < | 0.0301 | 4.017e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 235633 | dscfm | 9.3340627011 %H20, 14.393731406 %CO2, 5.2448223713 %O2, 274.83333333 Deg F |  | Concentration to EF conversion error. | BDL | BDL | 0.037435 | ug/dscm | 1.1369e-08 |  | 1 | 77901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 | < | 0.0284 | 3.858e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 237651 | dscfm | 9.3410276982 %H20, 14.404474131 %CO2, 5.2738044833 %O2, 273.86666667 Deg F |  | Concentration to EF conversion error. | BDL | BDL | 0.035958 | ug/dscm | 1.2226e-08 |  | 2 | 77901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 | < | 0.00975 | 1.288e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 238259 | dscfm | 9.4 %H20, 14.5 %CO2, 5.2 %O2, 272.3 Deg F |  | Conversion error due to incorrect mass. Concentration and EF changed. | BDL | BDL | 0.0059787 | ug/dscm | 1.1537e-08 |  | 3 | 77901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 | < | 0.0301 | 3.219e-05 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 246537 | dscfm | 9.3464218753 %H20, 12.909443402 %CO2, 6.93720472 %O2, 734.52333333 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm. | Concentration to EF conversion error. Other potential issues with OTM spreadsheet but insufficient data in docket files to confirm. | BDL | BDL | 0.03 | ug/dscm | 1.2516e-08 |  | BLRB R1 | 77902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 | < | 0.244 | 0.0003219 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 249027 | dscfm | 9.0331626568 %H20, 12.895945323 %CO2, 6.9703094476 %O2, 733.55666667 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm. | Concentration to EF conversion error. Other potential issues with OTM spreadsheet but insufficient data in docket files to confirm. | BDL | BDL | 0.3 | ug/dscm | 1.2613e-08 |  | BLRB R2 | 77902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 | < | 0.268 | 0.0003541 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 255597 | dscfm | 9.0200116335 %H20, 11.980561103 %CO2, 7.9318876933 %O2, 731.99 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm. | Concentration to EF conversion error. Other potential issues with OTM spreadsheet but insufficient data in docket files to confirm. | BDL | BDL | 0.33 | ug/dscm | 1.3852e-08 |  | BLRB R3 | 77902
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 |  | 1.31 | 0.001717 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 593113 | dscfm | 13 %H20, 12.5 %CO2, 6 %O2, 178 Deg F |  |  | ADL | ADL | 1.6 | ug/dscm | 1.31e-06 |  | 1 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 |  | 1.32 | 0.001642 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 579657 | dscfm | 13.1 %H20, 12.3 %CO2, 6.8 %O2, 178 Deg F |  |  | ADL | ADL | 1.53 | ug/dscm | 1.32e-06 |  | 2 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 |  | 1.36 | 0.001706 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 585852 | dscfm | 12.8 %H20, 12.7 %CO2, 6.1 %O2, 178 Deg F |  |  | ADL | ADL | 1.59 | ug/dscm | 1.36e-06 |  | 3 | 2027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 |  | 2.02 | 0.002554 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 590544 | dscfm | 13.9 %H20, 13.3 %CO2, 5.6 %O2, 178 Deg F |  |  | ADL | ADL | 2.38 | ug/dscm | 2.02e-06 |  | 1 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 |  | 2.2 | 0.002833 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 618616 | dscfm | 11.9 %H20, 12.7 %CO2, 6.1333333333 %O2, 178 Deg F |  |  | ADL | ADL | 2.64 | ug/dscm | 2.2e-06 |  | 2 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 |  | 2.18 | 0.002704 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 594930 | dscfm | 13.6 %H20, 13.4 %CO2, 5.7333333333 %O2, 178 Deg F |  |  | ADL | ADL | 2.52 | ug/dscm | 2.18e-06 |  | 3 | 2028
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 0.0375 | 4.834e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 717418 | dscfm | 12.5 %H20, 15.559967101 %CO2, 3.9 %O2, 330 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.045048 | ug/dscm | 3.38e-08 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 0.045 | 6.152e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 728890 | dscfm | 12.2 %H20, 15.523241735 %CO2, 3.9 %O2, 334 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.057331 | ug/dscm | 4.3e-08 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 0.0332 | 4.713e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 732026 | dscfm | 12 %H20, 15.430807294 %CO2, 4 %O2, 335 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.043927 | ug/dscm | 3.32e-08 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 0.0375 | 4.834e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 717418 | dscfm | 12.5 %H20, 15.559967101 %CO2, 3.9 %O2, 330 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.045048 | ug/dscm | 3.38e-08 |  | 1 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 0.045 | 6.152e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 728890 | dscfm | 12.2 %H20, 15.523241735 %CO2, 3.9 %O2, 334 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.057331 | ug/dscm | 4.3e-08 |  | 2 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 0.0332 | 4.713e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 732026 | dscfm | 12 %H20, 15.430807294 %CO2, 4 %O2, 335 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%. |  | ADL | ADL | 0.043927 | ug/dscm | 3.32e-08 |  | 3 | 2256
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 1 |  | 0.0311 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 406667 | dscfm | 6.6 %H20, 14.2 %CO2, 4.5 %O2, 286 Deg F |  |  | ADL | ADL | 0.04 | ug/dscm | 2.88e-08 |  | 1 | 1554
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 3 |  | 0.0156 | 2.146e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 401885 | dscfm | 6.4 %H20, 15.3 %CO2, 4.2 %O2, 288 Deg F |  | Incorrect conversion from concentration to emission | ADL | ADL | 0.02 | ug/dscm | 1.32e-08 |  | 3 | 1554
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 4 |  | 0.0311 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 404879 | dscfm | 6.3 %H20, 15.6 %CO2, 4.5 %O2, 297 Deg F |  |  | ADL | ADL | 0.04 | ug/dscm | 2.82e-08 |  | 4 | 1554
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 11.1 | 0.01271 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 216648 | dscfm | 6.42 %H20, 11.79 %CO2, 7.3 %O2, 337 Deg F |  | 1000x error in concentration; missing flag. |  | ADL | 11849 | ug/dscm | 1.11e-05 |  | M30B Run 1 | 2181
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 11.3 | 0.01314 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 212771 | dscfm | 6.2 %H20, 11.7 %CO2, 7.15 %O2, 341 Deg F |  | 1000x error in concentration; missing flag. |  | ADL | 12244 | ug/dscm | 1.13e-05 |  | M30B Run 2 | 2181
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 12 | 0.01391 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 207564 | dscfm | 6.24 %H20, 11.96 %CO2, 7.19 %O2, 337 Deg F |  | 1000x error in concentration; missing flag. |  | ADL | 12966 | ug/dscm | 1.2e-05 |  | M30B Run 3 | 2181
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F |  | Missing flag |  | ADL | 10.63 | ug/dscm | 9.8e-06 |  | M30B Run 1 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F |  | Missing flag |  | ADL | 11.06 | ug/dscm | 1.01e-05 |  | M30B Run 2 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F |  | Missing flag |  | ADL | 9.65 | ug/dscm | 8.85e-06 |  | M30B Run 3 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F |  | Missing flag |  | ADL | 10.63 | ug/dscm | 9.8e-06 |  | M30B Run 1 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F |  | Missing flag |  | ADL | 11.06 | ug/dscm | 1.01e-05 |  | M30B Run 2 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F |  | Missing flag |  | ADL | 9.65 | ug/dscm | 8.85e-06 |  | M30B Run 3 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F |  | Missing flag |  | ADL | 10.63 | ug/dscm | 9.8e-06 |  | M30B Run 1 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F |  | Missing flag |  | ADL | 11.06 | ug/dscm | 1.01e-05 |  | M30B Run 2 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F |  | Missing flag |  | ADL | 9.65 | ug/dscm | 8.85e-06 |  | M30B Run 3 | 2182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.676 | 0.0008473 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 508239 | dscfm | 12.9 %H20, 12.1 %CO2, 6.2 %O2, 73 Deg F |  |  | ADL | ADL | 0.7897 | ug/dscm | 6.76e-07 |  | 1 | 1741
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.633 | 0.0008005 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 506246 | dscfm | 12.9 %H20, 12.2 %CO2, 6.1 %O2, 78 Deg F |  |  | ADL | ADL | 0.746 | ug/dscm | 6.33e-07 |  | 3 | 1741
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 5 |  | 0.702 | 0.0008816 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 506195 | dscfm | 12.9 %H20, 12.3 %CO2, 5.9 %O2, 81 Deg F |  |  | ADL | ADL | 0.8216 | ug/dscm | 7.02e-07 |  | 5 | 1741
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.24 | 0.001633 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 510586 | dscfm | 12.6 %H20, 12.8 %CO2, 5.4 %O2, 126 Deg F |  |  | ADL | ADL | 1.522 | ug/dscm | 1.24e-06 |  | 1 | 1744
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 1.09 | 0.001424 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 501186 | dscfm | 13.5 %H20, 12.6 %CO2, 5.6 %O2, 125 Deg F |  |  | ADL | ADL | 1.3274 | ug/dscm | 1.09e-06 |  | 3 | 1744
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 5 |  | 1.5 | 0.001966 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 504970 | dscfm | 12.8 %H20, 12.8 %CO2, 5.5 %O2, 125 Deg F |  |  | ADL | ADL | 1.8324 | ug/dscm | 1.5e-06 |  | 5 | 1744
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 5.13 | 0.006653 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature |  | ADL | DLL | 6048.3294 | ng/dscm | 5.1279e-06 | [ | 1 | 1151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 4.66 | 0.006024 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature |  | ADL | DLL | 5476.6133 | ng/dscm | 4.6617e-06 | [ | 2 | 1151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 6.81 | 0.008613 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature |  | ADL | DLL | 7829.9036 | ng/dscm | 6.8097e-06 | [ | 3 | 1151
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 1 | < | 0.0128 | 1.623e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 14.7537 | ng/dscm | 1.283e-08 | [<1.13] | 1 | 1052
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 2 | < | 0.0139 | 1.746e-05 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 15.8704 | ng/dscm | 1.3857e-08 | [<.147] | 2 | 1052
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 3 | < | 0.0197 | 2.49e-05 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 22.6389 | ng/dscm | 1.9741e-08 | [<.883] | 3 | 1052
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.117 | 0.000162 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 864027 | dscfm | 11.93 %H20, 15.21 %CO2, 4.39 %O2, 289.4 Deg F |  |  | ADL | ADL | 0.151 | ug/dscm | 1.17e-07 |  | BHS3-M30B-R2 | 1619
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.122 | 0.0001695 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 864027 | dscfm | 11.93 %H20, 15.21 %CO2, 4.39 %O2, 289.4 Deg F |  |  | ADL | ADL | 0.158 | ug/dscm | 1.22e-07 |  | BHS3-M30B-R3 | 1619
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.126 | 0.0001738 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 865350 | dscfm | 12.29 %H20, 15.22 %CO2, 4.45 %O2, 290.4 Deg F |  |  | ADL | ADL | 0.162 | ug/dscm | 1.26e-07 |  | BHS3-M30B-R4 | 1619
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.284 | 0.0003541 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 140597 | dscfm | 8.04 %H20, 13.9 %CO2, 5.91 %O2, 364 Deg F |  | Incorrect mass units. | ADL | ADL | 330 | ug/dscm | 2.84e-07 |  | 1 | 199801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.266 | 0.0003326 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 137425 | dscfm | 8.56 %H20, 13.86 %CO2, 5.89 %O2, 366.9 Deg F |  | Incorrect mass units. | ADL | ADL | 310 | ug/dscm | 2.66e-07 |  | 2 | 199801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.24 | 0.0003004 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 138430 | dscfm | 8.94 %H20, 13.87 %CO2, 5.86 %O2, 368.8 Deg F |  | Incorrect mass units. | ADL | ADL | 280 | ug/dscm | 2.4e-07 |  | 3 | 199801
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.292 | 0.000397 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 135786 | dscfm | 6.56 %H20, 15.23 %CO2, 4.91 %O2, 372 Deg F |  | Incorrect mass units; flag missing. |  | ADL | 370 | ug/dscm | 2.92e-07 |  | 1 | 199802
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.284 | 0.0003755 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 135830 | dscfm | 6.57 %H20, 15.07 %CO2, 4.89 %O2, 372.2 Deg F |  | Incorrect mass units; flag missing. |  | ADL | 350 | ug/dscm | 2.84e-07 |  | 2 | 199802
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.279 | 0.0003755 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 134834 | dscfm | 7.12 %H20, 14.81 %CO2, 4.91 %O2, 373.2 Deg F |  | Incorrect mass units; flag missing. |  | ADL | 350 | ug/dscm | 2.79e-07 |  | 3 | 199802
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 1 |  | 0.0148 | 1.679e-05 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 |  |  |  | .0175, [ |  | DDL | DLL | 15.2645 | ng/dscm | 1.4775e-08 | .0175, [ | 1 | 63254
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 2 |  | 0.0536 | 6.049e-05 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 54.9921 | ng/dscm | 5.3603e-08 | .020, .2345, [.01] | 2 | 63254
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 3 |  | 0.0618 | 6.914e-05 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 62.8517 | ng/dscm | 6.1783e-08 | .018, .267, [<.01] | 3 | 63254
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 2.97 | 0.003744 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 3403.8056 | ng/dscm | 2.9745e-06 | FH(1B)=[ | M29-1 | 1826
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 2.52 | 0.003157 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 2869.6474 | ng/dscm | 2.525e-06 | FH(1B)=[0.059],BH(2B)=[1.8],BH(3A)=[ | M29-2 | 1826
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 2.38 | 0.002949 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 2681.1902 | ng/dscm | 2.3756e-06 | FH(1B)=[ | M29-3 | 1826
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 1.45 | 0.001881 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1709.9672 | ng/dscm | 1.4544e-06 | FH(1B)=[ | M29-1 | 18261
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 1.62 | 0.002075 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 1886.7498 | ng/dscm | 1.6156e-06 | FH(1B)=[0.065],BH(2B)=[0.75],BH(3A)=[0.063].BH(3B)=[0.159],BH(3C)=[7.52] | M29-2 | 18261
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 1.86 | 0.002422 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 2201.7152 | ng/dscm | 1.8603e-06 | FH(1B)=[0.314],BH(2B)=[0.79],BH(3A)=[ | M29-3 | 18261
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 3.33 | 0.00418 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 338821 | dscfm | 7.1 %H20, 13.259 %CO2, 5.948 %O2, 273.33333333 Deg F |  |  | ADL | ADL | 3.896 | ug/dscm | 3.3251e-06 |  | 1 | 982
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 2.88 | 0.003616 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 338821 | dscfm | 7.1 %H20, 13.259 %CO2, 5.948 %O2, 277.58333333 Deg F |  |  | ADL | ADL | 3.37 | ug/dscm | 2.8761e-06 |  | 2 | 982
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 2.22 | 0.002798 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 338082 | dscfm | 7.2 %H20, 13.235 %CO2, 5.93 %O2, 273.58333333 Deg F |  |  | ADL | ADL | 2.608 | ug/dscm | 2.2231e-06 |  | 3 | 982
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 2.41 | 0.003032 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 338082 | dscfm | 7.2 %H20, 13.235 %CO2, 5.93 %O2, 280.5 Deg F |  |  | ADL | ADL | 2.826 | ug/dscm | 2.409e-06 |  | 4 | 982
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 4.66 | 0.005832 | mg/Nm3 | Unknown | 2010-03-25 | Refer to sample method | U.S. EPA Method 30B | 339979 | dscfm | 8.3 %H20, 13.404 %CO2, 6.029 %O2, 272.5 Deg F |  |  | ADL | ADL | 5.435 | ug/dscm | 4.6638e-06 |  | 5 | 982
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 10.4 | 0.01013 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 1840874 | dscfm | 6 %H20, 11 %CO2, 8.3 %O2, 289 Deg F |  | Missing flag |  | ADL | 9.44 | ug/dscm | 1.0448e-05 |  | 1 | 1007002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 7.21 | 0.008713 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1834426 | dscfm | 63.8 %H20, 11 %CO2, 8.3 %O2, 282.1 Deg F |  | Missing flag |  | ADL | 8.12 | ug/dscm | 7.2064e-06 |  | 2 | 1007002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.29 | 0.00662 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1719505 | dscfm | 10.1 %H20, 11.1 %CO2, 8.3 %O2, 299.8 Deg F |  | Missing flag |  | ADL | 6.17 | ug/dscm | 5.2917e-06 |  | 3 | 1007002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0259 | 4.569e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 254273 | dscfm | 6.7 %H20, 13.7 %CO2, 4.96 %O2, 338 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 4.258e-05 | ug/dscm | 2.5942e-08 |  | 1 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0152 | 2.678e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 257589 | dscfm | 10 %H20, 13.4 %CO2, 5.09 %O2, 336 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 2.4955e-05 | ug/dscm | 1.5204e-08 |  | 2 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0256 | 4.503e-05 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 253299 | dscfm | 9.6 %H20, 13.5 %CO2, 5.27 %O2, 332 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 4.1969e-05 | ug/dscm | 2.5568e-08 |  | 3 | 1086
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0183 | 3.219e-05 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 275612 | dscfm | 13.6 %CO2, %O2, 324 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 3.0036e-05 | ug/dscm | 1.83e-08 |  | 1 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0206 | 3.627e-05 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 277164 | dscfm | 13.7 %CO2, 324 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 3.3787e-05 | ug/dscm | 2.0585e-08 |  | 2 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0182 | 3.207e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 269532 | dscfm | 13.8 %CO2, %O2, 318 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 2.9885e-05 | ug/dscm | 1.8208e-08 |  | 3 | 1088
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0284 | 5.457e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 246293 | dscfm | 12.7 %CO2, 5.8 %O2, 329 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 5.086e-05 | ug/dscm | 2.8421e-08 |  | 1 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0239 | 4.218e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 247170 | dscfm | 13 %CO2, 5.7 %O2, 332 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 3.9314e-05 | ug/dscm | 2.3936e-08 |  | 2 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0271 | 4.262e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 246467 | dscfm | 13.1 %CO2, 5.6 %O2, 331 Deg F |  | Suspect the volumes reported in liters not dscm. Concentrations off by 1000x. Original emission rates were assumed correct based on conversion. Concentrations were corrected. | ADL | ADL | 3.9719e-05 | ug/dscm | 2.7143e-08 |  | 3 | 1990
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 0.016 | 2.135e-05 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 336511 | dscfm | 11.92 %H20, 14.7 %CO2, 5.34 %O2, 180.4 Deg F |  | Flag missing assumed to be ADL based on total Hg masses reported. |  | ADL | 0.0199 | ug/dscm | 1.6e-08 |  | 1 | 1150
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0235 | 3.122e-05 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 310424 | dscfm | 12.34 %H20, 14.11 %CO2, 5.43 %O2, 181.5 Deg F |  | Missing flag |  | ADL | 0.0291 | ug/dscm | 2.351e-08 |  | 2 | 1150
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0184 | 2.457e-05 | mg/Nm3 | Unknown | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 311350 | dscfm | 11.76 %H20, 13.75 %CO2, 5.34 %O2, 178.8 Deg F |  | Flag missing assumed to be ADL based on total Hg masses reported. |  | ADL | 0.0229 | ug/dscm | 1.841e-08 |  | 3 | 1150
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0359 | 4.775e-05 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 318031 | dscfm | 13.19 %H20, 14.58 %CO2, 5.24 %O2, 179.8 Deg F |  | Missing flag |  | ADL | 0.0445 | ug/dscm | 3.587e-08 |  | 1 | 1252
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0279 | 2.479e-05 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 322994 | dscfm | 12.91 %H20, 14.99 %CO2, 4.79 %O2, 178.3 Deg F |  | Missing flag |  | ADL | 0.0231 | ug/dscm | 2.79e-08 |  | 2 | 1252
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0376 | 3.337e-05 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 323103 | dscfm | 12.99 %H20, 14.58 %CO2, 5.29 %O2, 179.3 Deg F |  | Missing flag |  | ADL | 0.0311 | ug/dscm | 3.76e-08 |  | 3 | 1252
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 |  | 3.13 | 0.004271 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 662681 | dscfm | 14.4 %H20, 15.02 %CO2, 4.65 %O2, 120.9 Deg F |  |  | ADL | ADL | 3.98 | ug/dscm | 3.125e-06 |  | 1 | 1670
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 |  | 3.19 | 0.004405 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 662142 | dscfm | 14.5 %H20, 14.88 %CO2, 4.48 %O2, 121 Deg F |  |  | ADL | ADL | 4.105 | ug/dscm | 3.1898e-06 |  | 2 | 1670
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 |  | 3.52 | 0.004839 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 660266 | dscfm | 14.7 %H20, 15.5 %CO2, 4.54 %O2, 121.6 Deg F |  |  | ADL | ADL | 4.51 | ug/dscm | 3.5173e-06 |  | 3 | 1670
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 |  | 1.44 | 0.00191 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 849901 | dscfm | 15.5 %H20, 16.47 %CO2, 5.18 %O2, 123.8 Deg F |  |  | ADL | ADL | 1.78 | ug/dscm | 1.4447e-06 |  | 1 | 1655
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 |  | 1.73 | 0.002285 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 855052 | dscfm | 15.4 %H20, 14.88 %CO2, 5.2 %O2, 123.4 Deg F |  |  | ADL | ADL | 2.13 | ug/dscm | 1.731e-06 |  | 2 | 1655
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 |  | 2.02 | 0.002672 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 840622 | dscfm | 15.2 %H20, 15.75 %CO2, 5.15 %O2, 122.8 Deg F |  |  | ADL | ADL | 2.49 | ug/dscm | 2.0172e-06 |  | 3 | 1655
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 1 |  | 0.34 | 0.0004077 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1046703 | dscfm | 5.2 %H20, 6.6 %CO2, 13.4 %O2, 198 Deg F |  |  | ADL | ADL | 0.38 | ug/dscm | 3.4001e-07 |  | 1 | 1007003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 2 | < | 0.202 | 0.0002468 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 993033 | dscfm | 12.5 %H20, 6.5 %CO2, 13.4 %O2, 200.5 Deg F |  |  | BDL | BDL | [<0.23] | ug/dscm |  |  | 2 | 1007003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 3 | < | 0.141 | 0.0001717 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 503173 | dscfm | 8.9 %H20, 13.8 %CO2, 4.9 %O2, 313.7 Deg F |  |  | BDL | BDL | [<0.16] | ug/dscm |  |  | 3 | 1007003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 4 | < | 0.226 | 0.0003112 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 495017 | dscfm | 8.4 %H20, 13.9 %CO2, 4.7 %O2, 305.7 Deg F |  |  | BDL | BDL | [<0.29] | ug/dscm |  |  | 4 | 1007003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0202 | 2.468e-05 | mg/Nm3 | Unknown | 2010-03-29 | Refer to sample method | U.S. EPA Method 30B | 1070269 | dscfm | 13.27 %H20, 12.777 %CO2, 6.212 %O2, 124.8 Deg F |  | Missing flag |  | ADL | 0.023 | ug/dscm | 2.0228e-08 |  | 1 | 1536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.0149 | 1.931e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 1043417 | dscfm | 12.97 %H20, 13.603 %CO2, 5.37 %O2, 122.7 Deg F |  | Changed flag from missing to ADL |  | ADL | 0.018 | ug/dscm | 1.4869e-08 |  | 2 | 1536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0256 | 3.219e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 1085103 | dscfm | 12.87 %H20, 13.167 %CO2, 6.02 %O2, 122.9 Deg F |  | Missing flag |  | ADL | 0.03 | ug/dscm | 2.5603e-08 |  | 3 | 1536
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0256 | 2.897e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 1120748 | dscfm | 12.89 %H20, 11.862175 %CO2, 6 %O2, 127.83585 Deg F |  |  | ADL | ADL | 0.027 | ug/dscm | 2.5577e-08 |  | 1 | 1537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.0326 | 3.756e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 1079195 | dscfm | 12.85 %H20, 12.0636 %CO2, 6 %O2, 128.56852 Deg F |  |  | ADL | ADL | 0.035 | ug/dscm | 3.2602e-08 |  | 2 | 1537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0881 | 9.979e-05 | mg/Nm3 | Unknown | 2010-04-02 | Refer to sample method | U.S. EPA Method 30B | 1058382 | dscfm | 13.64 %H20, 11.8676 %CO2, 6 %O2, 130.42712 Deg F |  |  | ADL | ADL | 0.093 | ug/dscm | 8.8059e-08 |  | 3 | 1537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.81 | 0.000882 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.71 %H20, 11.59 %CO2, 7.95 %O2, 372 Deg F |  |  | ADL | ADL | 0.822 | ug/dscm | 8.1e-07 |  | 1 | 2275
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.7 | 0.0007414 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.96 %H20, 11.3 %CO2, 8.26 %O2, 376 Deg F |  |  | ADL | ADL | 0.691 | ug/dscm | 7e-07 |  | 2 | 2275
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.423 | 0.0004635 | mg/Nm3 | Unknown | 2010-05-27 | Refer to sample method | U.S. EPA Method 30B |  |  | 9.41 %H20, 11.59 %CO2, 7.87 %O2, 372 Deg F |  |  | ADL | ADL | 0.432 | ug/dscm | 4.23e-07 |  | 3 | 2275
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.358 | 0.0003595 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 481133 | dscfm | 7.8 %H20, 10.67 %CO2, 8.95 %O2, 310.5 Deg F |  |  | ADL | ADL | 0.335 | ug/dscm | 3.58e-07 |  | 1 | 807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.577 | 0.0005901 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 477212 | dscfm | 7.6 %H20, 10.85 %CO2, 8.73 %O2, 303.8 Deg F |  |  | ADL | ADL | 0.55 | ug/dscm | 5.77e-07 |  | 2 | 807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.518 | 0.0005226 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 467926 | dscfm | 8.4 %H20, 10.72 %CO2, 8.91 %O2, 304.3 Deg F |  |  | ADL | ADL | 0.487 | ug/dscm | 5.18e-07 |  | 3 | 807
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.18 | 0.001437 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B | 1851508 | dscfm | 16 %H20, 13.063 %CO2, 6.569 %O2, 198.91666667 Deg F |  |  | ADL | ADL | 1.3392 | ug/dscm | 1.1784e-06 |  | 1 | 1559
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.971 | 0.001196 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1918056 | dscfm | 15.5 %H20, 13.159 %CO2, 6.493 %O2, 193.08333333 Deg F |  |  | ADL | ADL | 1.1145 | ug/dscm | 9.7105e-07 |  | 2 | 1559
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1 | 0.001214 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1911626 | dscfm | 16.5 %H20, 12.97 %CO2, 6.72 %O2, 192.54166667 Deg F |  |  | ADL | ADL | 1.1311 | ug/dscm | 1.0011e-06 |  | 3 | 1559
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.072 | 9.174e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 278182 | dscfm | 7.53 %H20, 14.91 %CO2, 4.91 %O2, 321.6 Deg F |  | Missing flag |  | ADL | 0.0855 | ug/dscm | 7.195e-08 |  | 1 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.0709 | 8.96e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 278977 | dscfm | 7.26 %H20, 14.8 %CO2, 5.04 %O2, 321.26 Deg F |  | Missing flag |  | ADL | 0.0835 | ug/dscm | 7.085e-08 |  | 2 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.0719 | 9.228e-05 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B | 260530 | dscfm | 7.94 %H20, 14.89 %CO2, 4.92 %O2, 321.81 Deg F |  | Missing flag |  | ADL | 0.086 | ug/dscm | 7.19e-08 |  | 3 | 1294
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 0.351 | 0.0004389 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 887000 | dscfm | 13.4 %H20, %CO2, 174 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.51e-07 |  | Sample 1 | 1451
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 0.859 | 0.001073 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 920000 | dscfm | 13.3 %H20, 178 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 8.59e-07 |  | Sample 2 | 1451
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 0.254 | 0.0003176 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 827000 | dscfm | 12.2 %H20, %CO2, 171 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 2.54e-07 |  | Sample 3 | 1451
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 2 |  | 11.7 | 0.01163 | mg/Nm3 | Unknown | 2010-06-28 | Refer to sample method | U.S. EPA Method 30B | 474066 | dscfm | 28.5 %H20, 10.7 %CO2, 9 %O2, 285.1 Deg F |  |  | ADL | ADL | 10.84 | ug/dscm | 1.1699e-05 |  | 2 | 1289001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 3 |  | 12.1 | 0.01189 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 391610 | dscfm | 27.8 %H20, 10.3 %CO2, 9.1 %O2, 278.8 Deg F |  |  | ADL | ADL | 11.08 | ug/dscm | 1.2061e-05 |  | 3 | 1289001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 5 |  | 11.1 | 0.01096 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 398635 | dscfm | 27.7 %H20, 10.4 %CO2, 9.1 %O2, 277.2 Deg F |  |  | ADL | ADL | 10.21 | ug/dscm | 1.1116e-05 |  | 5 | 1289001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.73 | 0.0008609 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 782.6292 | ng/dscm | 7.2991e-07 | ([ | M29-R1 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.68 | 0.0008172 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 742.8928 | ng/dscm | 6.8042e-07 | (0.016, 0.666, 0.179, 0.040, 3.35) | M29-R2 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.654 | 0.0008041 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 730.9904 | ng/dscm | 6.5356e-07 | DLL; ([ | M29-R3 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.73 | 0.0008609 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 782.6292 | ng/dscm | 7.2991e-07 | ([ | M29-R1 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.68 | 0.0008172 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 742.8928 | ng/dscm | 6.8042e-07 | (0.016, 0.666, 0.179, 0.040, 3.35) | M29-R2 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.654 | 0.0008041 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 730.9904 | ng/dscm | 6.5356e-07 | DLL; ([ | M29-R3 | 1642
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0149 | 1.794e-05 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 16.3116 | ng/dscm | 1.4886e-08 | #1 [ | 1 | 1249
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.174 | 0.0002105 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 191.3577 | ng/dscm | 1.7439e-07 | #1 [ | 2 | 1249
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0222 | 2.668e-05 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 24.2551 | ng/dscm | 2.2215e-08 | #1 [ | 3 | 1249
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.286 | 0.0003219 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 11.7 %CO2, 7.2 %O2, Deg F |  |  | ADL | ADL | 0.3 | ug/dscm | 2.86e-07 |  | 1 | 1309
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.272 | 0.0003112 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 11.7 %CO2, 7.2 %O2, Deg F |  |  | ADL | ADL | 0.29 | ug/dscm | 2.72e-07 |  | 2 | 1309
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.229 | 0.0002682 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 13.2 %H20, 12.2 %CO2, 6.7 %O2, Deg F |  |  | ADL | ADL | 0.25 | ug/dscm | 2.29e-07 |  | 3 | 1309
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.118 | 0.0001288 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %H20, 12 %CO2, 7.8 %O2, Deg F |  |  | ADL | ADL | 0.12 | ug/dscm | 1.18e-07 |  | 4 | 1309
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0471 | 5.365e-05 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.4 %H20, 12 %CO2, 6.9 %O2, Deg F |  |  | ADL | ADL | 0.05 | ug/dscm | 4.71e-08 |  | 1 | 1329
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0967 | 0.000118 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.4 %H20, 12 %CO2, 6.9 %O2, Deg F |  |  | ADL | ADL | 0.11 | ug/dscm | 9.67e-08 |  | 2 | 1329
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0415 | 4.292e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %H20, 12.1 %CO2, 7.3 %O2, Deg F |  |  | ADL | ADL | 0.04 | ug/dscm | 4.15e-08 |  | 3 | 1329
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.0732 | 8.584e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %H20, 12.1 %CO2, 7.3 %O2, Deg F |  |  | ADL | ADL | 0.08 | ug/dscm | 7.32e-08 |  | 4 | 1329
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 5 |  | 0.0811 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %H20, 12 %CO2, 6.7 %O2 |  |  | ADL | ADL | 0.09 | ug/dscm | 8.11e-08 |  | 5 | 1329
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 9.9e-07 |  | Sample 1 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8e-07 |  | Sample 2 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.82e-07 |  | Sample 3 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 9.9e-07 |  | Sample 1 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8e-07 |  | Sample 2 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.82e-07 |  | Sample 3 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 9.9e-07 |  | Sample 1 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8e-07 |  | Sample 2 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.82e-07 |  | Sample 3 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 9.9e-07 |  | Sample 1 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8e-07 |  | Sample 2 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.82e-07 |  | Sample 3 | 1895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.152 | 0.0001609 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1681900 | dscfm | 12.9 %H20, 11.08 %CO2, 8.32 %O2, 147.8 Deg F |  |  | ADL | ADL | 0.15 | ug/dscm | 1.52e-07 |  | Run 1 | 846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.144 | 0.0001502 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1652433 | dscfm | 12.8 %H20, 10.99 %CO2, 8.47 %O2, 147.6 Deg F |  |  | ADL | ADL | 0.14 | ug/dscm | 1.44e-07 |  | Run 2 | 846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.155 | 0.0001609 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1693683 | dscfm | 12.2 %H20, 10.88 %CO2, 8.58 %O2, 147.9 Deg F |  |  | ADL | ADL | 0.15 | ug/dscm | 1.55e-07 |  | Run 3 | 846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 0.232 | 0.0003155 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1334850 | dscfm | 15.2 %H20, 14.46 %CO2, 4.93 %O2, 129.9 Deg F |  |  | ADL | ADL | 0.294 | ug/dscm | 2.32e-07 |  | 1 | 1027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 0.232 | 0.000308 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1344500 | dscfm | 15.1 %H20, 14.36 %CO2, 4.95 %O2, 129.1 Deg F |  |  | ADL | ADL | 0.287 | ug/dscm | 2.32e-07 |  | 2 | 1027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 0.223 | 0.0003037 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1342567 | dscfm | 14.9 %H20, 14.38 %CO2, 4.91 %O2, 130 Deg F |  |  | ADL | ADL | 0.283 | ug/dscm | 2.23e-07 |  | 3 | 1027
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 0.308 | 0.0003863 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1381117 | dscfm | 14.9 %H20, 13.5 %CO2, 5.99 %O2, 127.9 Deg F |  |  | ADL | ADL | 0.36 | ug/dscm | 3.08e-07 |  | 1 | 1020
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 0.266 | 0.0003326 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1373950 | dscfm | 14.4 %H20, 13.4 %CO2, 6.01 %O2, 127.3 Deg F |  |  | ADL | ADL | 0.31 | ug/dscm | 2.66e-07 |  | 2 | 1020
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 0.256 | 0.0003219 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1398133 | dscfm | 14.4 %H20, 13.18 %CO2, 5.94 %O2, 127.3 Deg F |  |  | ADL | ADL | 0.3 | ug/dscm | 2.56e-07 |  | 3 | 1020
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 3.37 | 0.004217 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 867953 | dscfm | 5.5 %H20, 65 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.37e-06 |  | 1 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 3.53 | 0.00441 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 843587 | dscfm | 6.5 %H20, %CO2, %O2, 58 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.53e-06 |  | 3 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 3.21 | 0.004013 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 852628 | dscfm | 6.1 %H20, %CO2, %O2, 76 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.21e-06 |  | 5 | 975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 1.44 | 0.001502 | mg/Nm3 | Unknown | 2010-04-05 | Refer to sample method | U.S. EPA Method 30B | 227767 | dscfm | 6.12 %H20, 10.4 %CO2, 8.4 %O2, 316 Deg F |  |  | ADL | ADL | 1.4 | ug/dscm | 1.44e-06 |  | 1 | 996
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 1.58 | 0.001717 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 232147 | dscfm | 5.66 %H20, 10.4 %CO2, 8.4 %O2, 308 Deg F |  |  | ADL | ADL | 1.6 | ug/dscm | 1.58e-06 |  | 2 | 996
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 1.75 | 0.001824 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 227224 | dscfm | 5.94 %H20, 10.2 %CO2, 8.5 %O2, 317 Deg F |  |  | ADL | ADL | 1.7 | ug/dscm | 1.75e-06 |  | 3 | 996
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.72 | 0.0008906 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 383635 | dscfm | 15.6 %H20, 12.3 %CO2, 6.3 %O2, 130.2 Deg F |  |  | ADL | ADL | 0.83 | ug/dscm | 7.2021e-07 |  | 2 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.449 | 0.0005365 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 384645 | dscfm | 15.6 %H20, 12 %CO2, 6.8 %O2, 129.1 Deg F |  |  | ADL | ADL | 0.5 | ug/dscm | 4.4946e-07 |  | 4 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.72 | 0.000913 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 29 |  |  |  |  | Added EF and conc results from docket report; changed flag as per docket report |  | ADL |  | ng/dscm | 7.2021e-07 |  | 1 | 511
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.548 | 0.000671 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 29 |  |  |  |  | Added EF and conc results from docket report; changed flag as per docket report |  | ADL |  | ng/dscm | 5.484e-07 |  | 2 | 511
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.449 | 0.00055 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 29 |  |  |  |  | Added EF and conc results from docket report; changed flag as per docket report |  | ADL |  | ng/dscm | 4.4946e-07 |  | 3 | 511
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.548 | 0.0006545 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 383568 | dscfm | 15.7 %H20, 12 %CO2, 6.8 %O2, 129.9 Deg F |  |  | ADL | ADL | 0.61 | ug/dscm | 5.484e-07 |  | 3 | 1204
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 2 |  | 3.22 | 0.004056 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1050000 | dscfm | 18 %H20, 13 %CO2, 6.1 %O2, 135 Deg F |  |  | ADL | ADL | 3.78 | ug/dscm | 3.22e-06 |  | 2 | 1816
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 3 |  | 2.97 | 0.003745 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1050000 | dscfm | 18 %H20, 13 %CO2, 6.1 %O2, 135 Deg F |  |  | ADL | ADL | 3.49 | ug/dscm | 2.97e-06 |  | 3 | 1816
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 4 |  | 3.06 | 0.003595 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1080000 | dscfm | 17 %H20, 12.4 %CO2, 6.7 %O2, 135 Deg F |  |  | ADL | ADL | 3.35 | ug/dscm | 3.06e-06 |  | 4 | 1816
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1.73 | 0.002017 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 1.8799 | ug/dscm | 1.731e-06 |  | 3 | 537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.621 | 0.0007639 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 0.71194 | ug/dscm | 6.206e-07 |  | 4 | 537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 0.67 | 0.0008181 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 0.7624 | ug/dscm | 6.702e-07 |  | 5 | 537
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.976 | 0.001125 | mg/Nm3 | Unknown | 2010-04-19 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 1.0486 | ug/dscm | 9.7591e-07 |  | Sample 1 | 539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1.03 | 0.001164 | mg/Nm3 | Unknown | 2010-04-19 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 1.0849 | ug/dscm | 1.0343e-06 |  | Sample 2 | 539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.405 | 0.000481 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 0.4483 | ug/dscm | 4.0501e-07 |  | Sample 3 | 539
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 4.26 | 0.004652 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 218130 | dscfm | 9.1 %H20, 11.2 %CO2, 7.9 %O2, 292 Deg F |  |  | ADL | ADL | 4.3352 | ug/dscm | 4.2553e-06 |  | 1 | 1182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 3.42 | 0.003734 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 218130 | dscfm | 9.1 %H20, 11.2 %CO2, 7.9 %O2, 292 Deg F |  |  | ADL | ADL | 3.4796 | ug/dscm | 3.4155e-06 |  | 2 | 1182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 3.77 | 0.003864 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 219978 | dscfm | 9.3 %H20, 10.4 %CO2, 8.7 %O2, 287 Deg F |  |  | ADL | ADL | 3.6012 | ug/dscm | 3.7666e-06 |  | 3 | 1182
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.554 | 0.0005751 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1808404 | dscfm | 14.9 %H20, 11.1 %CO2, 8.56 %O2, 127.1 Deg F |  |  | ADL | ADL | 0.536 | ug/dscm | 5.54e-07 |  | 1 | 2056
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.684 | 0.0007103 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1806975 | dscfm | 14.9 %H20, 11.06 %CO2, 8.55 %O2, 127.4 Deg F |  |  | ADL | ADL | 0.662 | ug/dscm | 6.84e-07 |  | 2 | 2056
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.714 | 0.0007393 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1807286 | dscfm | 14.82 %H20, 11.01 %CO2, 8.59 %O2, 127 Deg F |  |  | ADL | ADL | 0.689 | ug/dscm | 7.14e-07 |  | 3 | 2056
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 3.03 | 0.002897 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F |  |  | ADL | ADL | 2.7 | ug/dscm | 3.03e-06 |  | 1 | 1806001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 2.91 | 0.00279 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F |  |  | ADL | ADL | 2.6 | ug/dscm | 2.91e-06 |  | 2 | 1806001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 2.42 | 0.002318 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F |  |  | ADL | ADL | 2.16 | ug/dscm | 2.42e-06 |  | 3 | 1806001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 1.45 | 0.001363 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 344.2 Deg F |  |  | ADL | ADL | 1.27 | ug/dscm | 1.45e-06 |  | 1 | 1806003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 1.89 | 0.001781 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 321.2 Deg F |  |  | ADL | ADL | 1.66 | ug/dscm | 1.89e-06 |  | 2 | 1806003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 1.37 | 0.001288 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 322.5 Deg F |  |  | ADL | ADL | 1.2 | ug/dscm | 1.37e-06 |  | 3 | 1806003
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0127 | 1.77e-05 | mg/Nm3 | Unknown | 2010-07-28 | Refer to sample method | U.S. EPA Method 30B | 163045 | dscfm | 9.13 %H20, 15.77 %CO2, 3.74 %O2, 327 Deg F |  |  | ADL | ADL | 0.0165 | ug/dscm | 1.255e-08 |  | 1 | 1893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0118 | 1.609e-05 | mg/Nm3 | Unknown | 2010-07-28 | Refer to sample method | U.S. EPA Method 30B | 163045 | dscfm | 9.13 %H20, 15.77 %CO2, 3.74 %O2, 330 Deg F |  |  | ADL | ADL | 0.015 | ug/dscm | 1.18e-08 |  | 2 | 1893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0131 | 1.824e-05 | mg/Nm3 | Unknown | 2010-07-29 | Refer to sample method | U.S. EPA Method 30B | 163656 | dscfm | 9.62 %H20, 15.95 %CO2, 3.71 %O2, 327 Deg F |  |  | ADL | ADL | 0.017 | ug/dscm | 1.31e-08 |  | 3 | 1893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 1.92 | 0.001989 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 961693 | dscfm | 13 %H20, 10.6 %CO2, 8.6 %O2, 214 Deg F |  |  | ADL | ADL | 1.854 | ug/dscm | 1.9219e-06 |  | 1 | 1848
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 1.5 | 0.001532 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 959176 | dscfm | 13 %H20, 10.4 %CO2, 8.8 %O2, 213 Deg F |  |  | ADL | ADL | 1.428 | ug/dscm | 1.5048e-06 |  | 2 | 1848
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.956 | 0.0009979 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 970409 | dscfm | 13 %H20, 10.9 %CO2, 8.5 %O2, 213.3125 Deg F |  |  | ADL | ADL | 0.93 | ug/dscm | 9.5628e-07 |  | 3 | 1848
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0782 | 0.0001073 | mg/Nm3 | Unknown | 2010-11-08 | Refer to sample method | U.S. EPA Method 30B | 1293717 | dscfm | 13.2 %H20, 14.4 %CO2, 4.3 %O2, 126.4 Deg F |  |  | ADL | ADL | 0.1 | ug/dscm | 7.82e-08 |  | 1 | 2323
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0655 | 7.511e-05 | mg/Nm3 | Unknown | 2010-11-09 | Refer to sample method | U.S. EPA Method 30B | 1280177 | dscfm | 13.6 %H20, 14.6 %CO2, 4.2 %O2, 127.6 Deg F |  |  | ADL | ADL | 0.07 | ug/dscm | 6.55e-08 |  | 2 | 2323
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0823 | 0.000118 | mg/Nm3 | Unknown | 2010-11-09 | Refer to sample method | U.S. EPA Method 30B | 1273325 | dscfm | 15.3 %H20, 14.6 %CO2, 4.2 %O2, 128.8 Deg F |  |  | ADL | ADL | 0.11 | ug/dscm | 8.23e-08 |  | 3 | 2323
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 1227.1762 | ng/dscm | 1.9894e-06 | FH .25, BH 6.84, FH Blank [<.12] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 670.958 | ng/dscm | 1.0579e-06 | FH .23, BH 3.78, FH Blank [<.12] | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 182.6999 | ng/dscm | 2.9235e-07 | FH .64, BH .436, FH Blank [<.12] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 1227.1762 | ng/dscm | 1.9894e-06 | FH .25, BH 6.84, FH Blank [<.12] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 670.958 | ng/dscm | 1.0579e-06 | FH .23, BH 3.78, FH Blank [<.12] | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 182.6999 | ng/dscm | 2.9235e-07 | FH .64, BH .436, FH Blank [<.12] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 1227.1762 | ng/dscm | 1.9894e-06 | FH .25, BH 6.84, FH Blank [<.12] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 670.958 | ng/dscm | 1.0579e-06 | FH .23, BH 3.78, FH Blank [<.12] | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 182.6999 | ng/dscm | 2.9235e-07 | FH .64, BH .436, FH Blank [<.12] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 1227.1762 | ng/dscm | 1.9894e-06 | FH .25, BH 6.84, FH Blank [<.12] | 1 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 670.958 | ng/dscm | 1.0579e-06 | FH .23, BH 3.78, FH Blank [<.12] | 2 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 |  |  |  |  | Re-calculated EF from concentration. | ADL | ADL | 182.6999 | ng/dscm | 2.9235e-07 | FH .64, BH .436, FH Blank [<.12] | 3 | 966
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.17 | 0.002792 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | BDL | DLL | 2537.7763 | ng/dscm | 2.173e-06 | [ | 1 | 942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.32 | 0.003044 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | BDL | DLL | 2767.0541 | ng/dscm | 2.3226e-06 | [ | 3 | 942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.75 | 0.003444 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | BDL | DLL | 3130.4871 | ng/dscm | 2.7545e-06 | [ | 2 | 942
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 5.56 | 0.00764 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | U.S. EPA Method 30B | 94232 | dscfm | 9.5 %H20, 14.7 %CO2, 4.9 %O2, 334 Deg F |  |  | ADL | ADL | 7.12 | ug/dscm | 5.56e-06 |  | 1 | 1846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 5.46 | 0.007178 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | U.S. EPA Method 30B | 98388 | dscfm | 9.6 %H20, 14.1 %CO2, 5.6 %O2, 341 Deg F |  |  | ADL | ADL | 6.69 | ug/dscm | 5.46e-06 |  | 2 | 1846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 5.39 | 0.007007 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | U.S. EPA Method 30B | 97307 | dscfm | 9.3 %H20, 13.5 %CO2, 5.7 %O2, 342 Deg F |  |  | ADL | ADL | 6.53 | ug/dscm | 5.39e-06 |  | 3 | 1846
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.428 | 0.0005479 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 1252777 | dscfm | 11.61 %H20, 13.85 %CO2, 5.67 %O2, 124.04166667 Deg F |  |  | ADL | ADL | 0.51065 | ug/dscm | 4.2785e-07 |  | 1 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.858 | 0.001111 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1248035 | dscfm | 12.04 %H20, 13.94 %CO2, 5.5 %O2, 124.20833333 Deg F |  |  | DLL | DLL | [<1.035] | ug/dscm |  |  | 2 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.928 | 0.001208 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1262491 | dscfm | 12.35 %H20, 13.91 %CO2, 5.41 %O2, 125.75 Deg F |  |  | ADL | ADL | 1.1262 | ug/dscm | 9.2776e-07 |  | 3 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.428 | 0.0005479 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 1252777 | dscfm | 11.61 %H20, 13.85 %CO2, 5.67 %O2, 124.04166667 Deg F |  |  | ADL | ADL | 0.51065 | ug/dscm | 4.2785e-07 |  | 1 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.858 | 0.001111 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1248035 | dscfm | 12.04 %H20, 13.94 %CO2, 5.5 %O2, 124.20833333 Deg F |  |  | DLL | DLL | [<1.035] | ug/dscm |  |  | 2 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.928 | 0.001208 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1262491 | dscfm | 12.7 %H20, 13.91 %CO2, 5.41 %O2, 125.75 Deg F |  |  | ADL | ADL | 1.1262 | ug/dscm | 9.2776e-07 |  | 3 | 901
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 6.5 | 0.007618 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 541060 | dscfm | 11.7 %H20, 12.72 %CO2, 6.97 %O2, 331.6 Deg F |  |  | DLL | DLL | 7.1 | ug/dscm | 6.5e-06 |  | 4 | 2185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 6.1 | 0.007189 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 550024 | dscfm | 10.4 %H20, 12.7 %CO2, 6.98 %O2, 336.2 Deg F |  |  | DLL | DLL | 6.7 | ug/dscm | 6.1e-06 |  | 5 | 2185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 6 |  | 6 | 0.006974 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 545582 | dscfm | 10.5 %H20, 12.72 %CO2, 6.98 %O2, 337.7 Deg F |  |  | DLL | DLL | 6.5 | ug/dscm | 6e-06 |  | 6 | 2185
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 4.93 | 0.00629 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.7 %O2, 295.79 Deg F |  |  | ADL | ADL | 5.8621 | ug/dscm | 4.93e-06 |  | 1 | 1959
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 6.16 | 0.007865 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.7 %O2, 290.79 Deg F |  |  | ADL | ADL | 7.3295 | ug/dscm | 6.16e-06 |  | 2 | 1959
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 6.21 | 0.007964 | mg/Nm3 | Unknown | 2010-03-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.8 %O2, 290.58 Deg F |  |  | ADL | ADL | 7.4223 | ug/dscm | 6.21e-06 |  | 3 | 1959
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 5.89 | 0.006978 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.8 %O2, 289 Deg F |  |  | ADL | ADL | 6.5036 | ug/dscm | 5.89e-06 |  | 1 | 1962
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 6.46 | 0.007594 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.9 %O2, 282.04 Deg F |  |  | ADL | ADL | 7.0777 | ug/dscm | 6.46e-06 |  | 2 | 1962
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.84 | 0.006916 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.7 %O2, 269.08 Deg F |  |  | ADL | ADL | 6.4454 | ug/dscm | 5.84e-06 |  | 3 | 1962
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1 | 0.001241 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1529688 | dscfm | 16.3 %H20, 13.19 %CO2, 6.18 %O2, 134.75 Deg F |  |  | DLL, Reporting limit based on MDL | DLL | [<1.157] | ug/dscm |  |  | 1 | 1317
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.835 | 0.001033 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1534516 | dscfm | 16.1 %H20, 13.23 %CO2, 6.18 %O2, 134.08333333 Deg F |  |  | DLL, Reporting limit based on MDL | DLL | [<0.963] | ug/dscm |  |  | 2 | 1317
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.812 | 0.001005 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1523991 | dscfm | 16.3 %H20, 13.2 %CO2, 6.17 %O2, 134.33333333 Deg F |  |  | DLL, Reporting limit based on MDL | DLL | [<0.937] | ug/dscm |  |  | 3 | 1317
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.899 | 0.001088 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B | 1621345 | dscfm | 16.4 %H20, 12.98 %CO2, 6.51 %O2, 134.25 Deg F |  |  | DLL | DLL | [<1.014] | ug/dscm |  |  | 1 | 1318
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.85 | 0.001038 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1593391 | dscfm | 16.7 %H20, 13.16 %CO2, 6.38 %O2, 134.58333333 Deg F |  |  | DLL | DLL | [<0.967] | ug/dscm |  |  | 2 | 1318
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.79 | 0.0009689 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1591911 | dscfm | 16.6 %H20, 13.23 %CO2, 6.32 %O2, 135.25 Deg F |  |  | DLL | DLL | [<0.903] | ug/dscm |  |  | 3 | 1318
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.643 | 0.0006921 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | U.S. EPA Method 30B | 298566 | dscfm | 8.2 %H20, 11.1 %CO2, 8.3 %O2, 369.3 Deg F |  |  | ADL | ADL | 0.645 | ug/dscm | 6.43e-07 |  | 1 | 1975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.684 | 0.0007296 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 304343 | dscfm | 8.2 %H20, 10.6 %CO2, 8.9 %O2, 359.2 Deg F |  |  | ADL | ADL | 0.68 | ug/dscm | 6.84e-07 |  | 2 | 1975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.808 | 0.0008691 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 299138 | dscfm | 8.2 %H20, 10.7 %CO2, 8.7 %O2, 363.8 Deg F |  |  | ADL | ADL | 0.81 | ug/dscm | 8.08e-07 |  | 3 | 1975
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.37 | 0.0003863 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 672028 | dscfm | 15.68 %H20, 10.4 %CO2, 8.4 %O2, 130 Deg F |  |  | ADL | ADL | 0.36 | ug/dscm | 3.7e-07 |  | 1 | 997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.459 | 0.0004828 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 672028 | dscfm | 15.68 %H20, 10.4 %CO2, 8.4 %O2, 130 Deg F |  |  | ADL | ADL | 0.45 | ug/dscm | 4.59e-07 |  | 2 | 997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.737 | 0.0007618 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 693034 | dscfm | 12.25 %H20, 10.3 %CO2, 8.6 %O2, 130 Deg F |  |  | ADL | ADL | 0.71 | ug/dscm | 7.37e-07 |  | 3 | 997
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 0.0743 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 577269 | dscfm | 12.74 %H20, 14.6 %CO2, 4.9 %O2, 170 Deg F |  |  | ADL | ADL | 0.09 | ug/dscm | 7.43e-08 |  | 2 | 1564
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 0.0709 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 585395 | dscfm | 12.44 %H20, 14.6 %CO2, 5 %O2, 158 Deg F |  |  | ADL | ADL | 0.09 | ug/dscm | 7.09e-08 |  | 3 | 1564
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 0.0708 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 577269 | dscfm | 12.74 %H20, 14.6 %CO2, 4.9 %O2, 170 Deg F |  |  | ADL | ADL | 0.09 | ug/dscm | 7.08e-08 |  | 1 | 1564
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 0.191 | 0.0002575 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 527403 | dscfm | 11.03 %H20, 14.3 %CO2, 5.1 %O2, 176 Deg F |  |  | ADL | ADL | 0.24 | ug/dscm | 1.91e-07 |  | 1 | 998
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 0.191 | 0.0002039 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 524523 | dscfm | 9.7 %H20, 10.4 %CO2, 8.4 %O2, 200 Deg F |  |  | ADL | ADL | 0.19 | ug/dscm | 1.91e-07 |  | 2 | 998
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 0.131 | 0.0001395 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 524523 | dscfm | 9.7 %H20, 10.2 %CO2, 8.5 %O2, 203 Deg F |  |  | ADL | ADL | 0.13 | ug/dscm | 1.31e-07 |  | 3 | 998
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 5.435e-07 |  | Sample 1 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.007e-07 |  | Sample 2 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.7069e-07 |  | Sample 3 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 5.435e-07 |  | Sample 1 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.007e-07 |  | Sample 2 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.7069e-07 |  | Sample 3 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 5.435e-07 |  | Sample 1 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.007e-07 |  | Sample 2 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.7069e-07 |  | Sample 3 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 5.435e-07 |  | Sample 1 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.007e-07 |  | Sample 2 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 6.7069e-07 |  | Sample 3 | 1985
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 3.75 | 0.004388 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 4.0894 | ug/dscm | 3.7549e-06 |  | 1 | 1173
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 3.21 | 0.003588 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 3.3439 | ug/dscm | 3.2131e-06 |  | 2 | 1173
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 4.44 | 0.005099 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 4.7525 | ug/dscm | 4.4421e-06 |  | 3 | 1173
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 1.07 | 0.001113 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 1.0376 | ug/dscm | 1.0745e-06 |  | 1 | 1172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 0.999 | 0.001084 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 1.0102 | ug/dscm | 9.9879e-07 |  | 2 | 1172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 0.892 | 0.0009421 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Missing flag |  | ADL | 0.87796 | ug/dscm | 8.9249e-07 |  | 3 | 1172
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 3.23 | 0.004464 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1158508 | dscfm | 13.54 %H20, 14.72 %CO2, 4.42 %O2, 125.1 Deg F |  |  | ADL | ADL | 4.16 | ug/dscm | 3.23e-06 |  | M30B 1 | 2183
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 3.07 | 0.004131 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1159417 | dscfm | 14.62 %H20, 14.29 %CO2, 4.82 %O2, 125.1 Deg F |  |  | ADL | ADL | 3.85 | ug/dscm | 3.07e-06 |  | M30B 2 | 2183
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.17 | 0.004335 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 181644 | dscfm | 14.5 %H20, 14.33 %CO2, 4.64 %O2, 125.8 Deg F |  |  | ADL | ADL | 4.04 | ug/dscm | 3.17e-06 |  | M30B 3 | 2183
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.153 | 0.0001953 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B | 2807920 | dscfm | 12.1 %H20, 9.9 %CO2, 6.8 %O2, 313 Deg F |  |  | DLL | DLL | 0.182 | ug/dscm | 1.53e-07 |  | 1 | 1723
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.172 | 0.0002146 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 3018141 | dscfm | 12.5 %H20, 9.9 %CO2, 6.9 %O2, 312.9 Deg F |  |  | DLL | DLL | 0.2 | ug/dscm | 1.72e-07 |  | 2 | 1723
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.154 | 0.0001931 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3722116 | dscfm | 12.3 %H20, 9.9 %CO2, 6.8 %O2, 307.6 Deg F |  |  | DLL | DLL | 0.18 | ug/dscm | 1.54e-07 |  | 3 | 1723
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 4.97 | 0.006352 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1291029 | dscfm | 14.75 %H20, 13.8 %CO2, 5.7 %O2, 185 Deg F |  |  | ADL | ADL | 5.92 | ug/dscm | 4.97e-06 |  | 1 | 1399
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 5.02 | 0.005998 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1257291 | dscfm | 14.69 %H20, 13.8 %CO2, 5.7 %O2, 186 Deg F |  |  | ADL | ADL | 5.59 | ug/dscm | 5.02e-06 |  | 2 | 1399
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 4 |  | 5.91 | 0.006599 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1262082 | dscfm | 14.79 %H20, 13.8 %CO2, 5.7 %O2, 185 Deg F |  |  | ADL | ADL | 6.15 | ug/dscm | 5.91e-06 |  | 4 | 1399
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.304 | 0.0003809 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 490000 | dscfm | 14.3 %H20, 165 Deg F |  | Incorrect concentration | ADL | ADL | 0.00029074 | ug/dscm | 3.0359e-07 |  | Sample 1 | 563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.445 | 0.000558 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 504000 | dscfm | 14.5 %H20, 166 Deg F |  | Incorrect concentration | ADL | ADL | 0.00035716 | ug/dscm | 4.45e-07 |  | Sample 2 | 563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.252 | 0.0003155 | mg/Nm3 | Unknown | 2010-02-19 | Refer to sample method | U.S. EPA Method 30B | 517000 | dscfm | 14 %H20, 165 Deg F |  | Incorrect concentration | ADL | ADL | 0.0002427 | ug/dscm | 2.52e-07 |  | Sample 3 | 563
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 0.549 | 0.0006889 | mg/Nm3 | Unknown | 2010-02-23 | Refer to sample method | U.S. EPA Method 30B | 591000 | dscfm | 12.9 %H20, 167 Deg F |  | Incorrect concentration | ADL | ADL | 0.00059601 | ug/dscm | 5.49e-07 |  | Sample 1 | 568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 0.588 | 0.0007372 | mg/Nm3 | Unknown | 2010-02-24 | Refer to sample method | U.S. EPA Method 30B | 594000 | dscfm | 13.3 %H20, 166 Deg F |  | Incorrect concentration | ADL | ADL | 0.00030135 | ug/dscm | 5.88e-07 |  | Sample 2 | 568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 0.518 | 0.0006492 | mg/Nm3 | Unknown | 2010-02-25 | Refer to sample method | U.S. EPA Method 30B | 587000 | dscfm | 13.3 %H20, 166 Deg F |  | Incorrect concentration | ADL | ADL | 0.00020061 | ug/dscm | 5.18e-07 |  | Sample 3 | 568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.955 | 0.001225 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 386007 | dscfm | 7.37 %H20, 13.44 %CO2, 5.64 %O2, 268.42 Deg F |  |  | ADL | ADL | 1.142 | ug/dscm | 9.55e-07 |  | 1 | 1755
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.396 | 0.0005075 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 386007 | dscfm | 7.37 %H20, 13.44 %CO2, 5.64 %O2, 274.75 Deg F |  |  | ADL | ADL | 0.473 | ug/dscm | 3.96e-07 |  | 2 | 1755
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.746 | 0.0009442 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 390701 | dscfm | 7.11 %H20, 13.24 %CO2, 5.85 %O2, 268.75 Deg F |  |  | ADL | ADL | 0.88 | ug/dscm | 7.46e-07 |  | 3 | 1755
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 0.902 | 0.001142 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 390701 | dscfm | 7.11 %H20, 13.24 %CO2, 5.85 %O2, 263.17 Deg F |  |  | ADL | ADL | 1.064 | ug/dscm | 9.02e-07 |  | 4 | 1755
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 0.301 | 0.0003831 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 383265 | dscfm | 7.37 %H20, 13.32 %CO2, 5.74 %O2, 262.92 Deg F |  |  | ADL | ADL | 0.357 | ug/dscm | 3.01e-07 |  | 5 | 1755
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.091 | 0.000117 | mg/Nm3 | Unknown | 2010-08-24 | Refer to sample method | U.S. EPA Method 30B | 800402 | dscfm | 12 %H20, 12 %CO2, 6 %O2, 361.5 Deg F |  |  | ADL | ADL | 0.109 | ug/dscm | 9.1e-08 |  | 1 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.184 | 0.0002361 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 762163 | dscfm | 11.1 %H20, 12.1 %CO2, 6.1 %O2, 358.5 Deg F |  |  | ADL | ADL | 0.22 | ug/dscm | 1.84e-07 |  | 2 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.21 | 0.0002661 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 767078 | dscfm | 11.4 %H20, 11.9 %CO2, 6.3 %O2, 360.6 Deg F |  |  | ADL | ADL | 0.248 | ug/dscm | 2.1e-07 |  | 3 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.091 | 0.000117 | mg/Nm3 | Unknown | 2010-08-24 | Refer to sample method | U.S. EPA Method 30B | 800402 | dscfm | 12 %H20, 12 %CO2, 6 %O2, 361.5 Deg F |  |  | ADL | ADL | 0.109 | ug/dscm | 9.1e-08 |  | 1 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.184 | 0.0002361 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 762163 | dscfm | 11.1 %H20, 12.1 %CO2, 6.1 %O2, 358.5 Deg F |  |  | ADL | ADL | 0.22 | ug/dscm | 1.84e-07 |  | 2 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.21 | 0.0002661 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 767078 | dscfm | 11.4 %H20, 11.9 %CO2, 6.3 %O2, 360.6 Deg F |  |  | ADL | ADL | 0.248 | ug/dscm | 2.1e-07 |  | 3 | 1885
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.73 | 0.006893 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 6266.366 | ng/dscm | 5.734e-06 | 0.0035, 1.77, 0.26, 18.6, 3.0, DL based on the std dev. Results of 7 blank analysis, FB front half = 0.0065, Back half = 0.0044 µg | M23-1 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.18 | 0.006538 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 5943.6502 | ng/dscm | 5.1797e-06 | 0.0045, 1.11, 0.17, 17.1, 2.6, DL based on the std dev. Results of 7 blank analysis, FB front half = 0.0065, Back half = 0.0044 µg | M23-2 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 6.82 | 0.008548 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 7770.6114 | ng/dscm | 6.8183e-06 | 0.0060, 2.85, 0.33, 20.5, 3.48, DL based on the std dev. Results of 7 blank analysis, FB front half = 0.0065, Back half = 0.0044 µg | M23-3 | 1141
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 |  | 0.0506 | 6.545e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 177882 | dscfm | 13.43 %H20, 13.55 %CO2, 5.55 %O2, 210.7 Deg F |  |  | ADL | ADL | 0.061 | ug/dscm | 5.0587e-08 |  | 1 | 695
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 |  | 0.0378 | 4.936e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 177690 | dscfm | 14.06 %H20, 13.66 %CO2, 5.4 %O2, 210.6 Deg F |  |  | ADL | ADL | 0.046 | ug/dscm | 3.7841e-08 |  | 2 | 695
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 |  | 0.0494 | 6.331e-05 | mg/Nm3 | Unknown | 2010-04-24 | Refer to sample method | U.S. EPA Method 30B | 175659 | dscfm | 14.03 %H20, 13.43 %CO2, 5.63 %O2, 213.2 Deg F |  |  | ADL | ADL | 0.059 | ug/dscm | 4.9366e-08 |  | 3 | 695
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0204 | 2.5e-05 | mg/Nm3 | Unknown | 2010-06-03 | Refer to sample method | U.S. EPA Method 30B | 692930 | dscfm | 9 %CO2, %O2, 192.2 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.021101 | ug/dscm | 1.5952e-08 |  | 1 | 1344
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.00729 | 8.906e-06 | mg/Nm3 | Unknown | 2010-06-04 | Refer to sample method | U.S. EPA Method 30B | 711516 | dscfm | 9.4 %CO2, %O2, 192.8 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0095497 | ug/dscm | 6.9285e-09 |  | 2 | 1344
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.00263 | 3.219e-06 | mg/Nm3 | Unknown | 2010-06-04 | Refer to sample method | U.S. EPA Method 30B | 711516 | dscfm | 9.4 %CO2, %O2, 192.8 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0038314 | ug/dscm | 2.7346e-09 |  | 3 | 1344
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 3.12 | 0.003809 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.12e-06 |  | Sample 1 | 1838
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 2.92 | 0.003562 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 2.92e-06 |  | Sample 2 | 1838
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.48 | 0.004249 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.48e-06 |  | Sample 3 | 1838
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.79 | 0.007889 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 7171.7433 | ng/dscm | 5.7912e-06 | FH(ADL) = 0.06 BH Fraction 1 (ADL) = 30.41 BH Fraction 2 (BDL) = 0.16, laboratory reporting limit BH Fraction 3 (ADL) = 3.7 Blank Corrected | 1 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 7.71 | 0.01064 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 9674.9567 | ng/dscm | 7.7149e-06 | FH(BDL) = 0.20, laboratory reporting limit BH Fraction 1 (ADL) = 41.3 BH Fraction 2 (BDL) = 0.15, laboratory reporting limit BH Fraction 3 (ADL) = 4.4 Blank Corrected | 2 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 5.83 | 0.008091 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 7355.3697 | ng/dscm | 5.8288e-06 | FH(BDL) = 0.20, laboratory reporting limit BH Fraction 1 (ADL) = 31.1 BH Fraction 2 (BDL) = 0.16, laboratory reporting limit BH Fraction 3 (ADL) = 3.7 Blank Corrected | 3 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.79 | 0.007889 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 7171.7433 | ng/dscm | 5.7912e-06 | FH(ADL) = 0.06 BH Fraction 1 (ADL) = 30.41 BH Fraction 2 (BDL) = 0.16, laboratory reporting limit BH Fraction 3 (ADL) = 3.7 Blank Corrected | 1 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 7.71 | 0.01064 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 9674.9567 | ng/dscm | 7.7149e-06 | FH(BDL) = 0.20, laboratory reporting limit BH Fraction 1 (ADL) = 41.3 BH Fraction 2 (BDL) = 0.15, laboratory reporting limit BH Fraction 3 (ADL) = 4.4 Blank Corrected | 2 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 5.83 | 0.008091 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 7355.3697 | ng/dscm | 5.8288e-06 | FH(BDL) = 0.20, laboratory reporting limit BH Fraction 1 (ADL) = 31.1 BH Fraction 2 (BDL) = 0.16, laboratory reporting limit BH Fraction 3 (ADL) = 3.7 Blank Corrected | 3 | 452145
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 4.27 | 0.005869 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and data flag missing. |  | ADL |  | ug/dscm | 4.27e-06 |  | Sample 1 | 203704
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 3.36 | 0.004625 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and data flag missing. |  | ADL |  | ug/dscm | 3.36e-06 |  | Sample 2 | 203704
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 3.38 | 0.004646 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and data flag missing. |  | ADL |  | ug/dscm | 3.38e-06 |  | Sample 3 | 203704
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 | < | 0.169 | 0.0002245 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 204.1076 | ng/dscm | 1.6899e-07 |  | 1 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 | < | 0.174 | 0.0002282 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 207.4962 | ng/dscm | 1.736e-07 |  | 2 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 | < | 0.166 | 0.0002205 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 200.4722 | ng/dscm | 1.6598e-07 |  | 3 | 1349
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.77 | 0.003221 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 2928.2242 | ng/dscm | 2.7674e-06 |  | M29-1 | 2135
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.79 | 0.003291 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 2991.4311 | ng/dscm | 2.7858e-06 |  | M29-2 | 2135
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 4 |  | 2.62 | 0.003139 | mg/Nm3 | Unknown | 2010-06-24 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 2853.8984 | ng/dscm | 2.6195e-06 |  | M29-4 | 2135
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.12 | 0.002484 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 2258.0001 | ng/dscm | 2.1183e-06 |  | M29-1 | 21351
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.67 | 0.003012 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 2738.2426 | ng/dscm | 2.6669e-06 |  | M29-2 | 21351
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 1.79 | 0.002042 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 1856.4116 | ng/dscm | 1.7943e-06 |  | M29-3 | 21351
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1.3 | 0.001609 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 686055 | dscfm | 12 %H20, 13.4 %CO2, 6.1 %O2, 300.5 Deg F |  |  | ADL | ADL | 1.5 | ug/dscm | 1.3e-06 |  | 1 | 2010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 0.935 | 0.001223 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 698344 | dscfm | 11.8 %H20, 13.7 %CO2, 5.8 %O2, 296 Deg F |  |  | ADL | ADL | 1.14 | ug/dscm | 9.35e-07 |  | 2 | 2010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1.01 | 0.001277 | mg/Nm3 | Unknown | 2010-06-17 | Refer to sample method | U.S. EPA Method 30B | 705100 | dscfm | 11.9 %H20, 13.4 %CO2, 6 %O2, 300.9 Deg F |  |  | ADL | ADL | 1.19 | ug/dscm | 8.52e-07 |  | 3 | 2010
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.44 | 0.001813 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | U.S. EPA Method 30B | 821000 | dscfm | 13.7 %H20, 13.2 %CO2, 5.8 %O2, 337 Deg F |  |  | ADL | ADL | 1.69 | ug/dscm | 1.44e-06 |  | 1 | 2102
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 2.46 | 0.003122 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B | 836000 | dscfm | 13.3 %H20, 13.2 %CO2, 5.7 %O2, 339 Deg F |  |  | ADL | ADL | 2.91 | ug/dscm | 2.46e-06 |  | 2 | 2102
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2.19 | 0.002801 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 832000 | dscfm | 13.3 %H20, 13.3 %CO2, 5.6 %O2, 339 Deg F |  |  | ADL | ADL | 2.61 | ug/dscm | 2.19e-06 |  | 3 | 2102
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 6.88 | 0.009142 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 1590359 | dscfm | 12.57 %H20, 14.11 %CO2, 5.3 %O2, 296.1 Deg F |  |  | ADL | ADL | 8.52 | ug/dscm | 6.88e-06 |  | 1 | 1381
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 4.93 | 0.006299 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 1562204 | dscfm | 13.09 %H20, 14.26 %CO2, 5.24 %O2, 297 Deg F |  |  | ADL | ADL | 5.87 | ug/dscm | 4.93e-06 |  | 2 | 1381
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 6.37 | 0.008208 | mg/Nm3 | Unknown | 2010-05-22 | Refer to sample method | U.S. EPA Method 30B | 1509097 | dscfm | 13.13 %H20, 13.77 %CO2, 4.99 %O2, 294 Deg F |  |  | ADL | ADL | 7.65 | ug/dscm | 6.37e-06 |  | 3 | 1381
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 4 |  | 5.66 | 0.00764 | mg/Nm3 | Unknown | 2010-05-22 | Refer to sample method | U.S. EPA Method 30B | 1509097 | dscfm | 13.13 %H20, 13.77 %CO2, 4.99 %O2, 294 Deg F |  |  | ADL | ADL | 7.12 | ug/dscm | 5.66e-06 |  | 4 | 1381
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.77 | 0.001985 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 269318 | dscfm | 10.6 %H20, 11.5 %CO2, 7.5 %O2, 342 Deg F |  |  | ADL | ADL | 1.85 | ug/dscm | 1.35e-06 |  | 1 | 893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 2.28 | 0.002554 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 259822 | dscfm | 10.7 %H20, 11.8 %CO2, 7.7 %O2, 336 Deg F |  |  | ADL | ADL | 2.38 | ug/dscm | 1.77e-06 |  | 2 | 893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.64 | 0.001835 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 266114 | dscfm | 10.7 %H20, 12 %CO2, 7.6 %O2, 328 Deg F |  |  | ADL | ADL | 1.71 | ug/dscm | 1.3e-06 |  | 3 | 893
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.12 | 0.005494 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F |  | Missing flag |  | ADL | 5.12 | ug/dscm | 4.12e-06 |  | WL3-30B-1 | 1855
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.14 | 0.006899 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F |  | Missing flag |  | ADL | 6.43 | ug/dscm | 5.14e-06 |  | WL3-30B-2 | 1855
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.72 | 0.004979 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F |  | Missing flag |  | ADL | 4.64 | ug/dscm | 3.72e-06 |  | WL3-30B-3 | 1855
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 7.38 | 0.008687 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 7896.9897 | ng/dscm | 7.3844e-06 | 0.013,0.18,0.0020,20.7,12.3 | 1 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 6.49 | 0.007685 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 6986.6278 | ng/dscm | 6.4858e-06 | 0.0072,0.11,0.0074,12.9,16.6 | 2 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 6.84 | 0.008111 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 7373.205 | ng/dscm | 6.8446e-06 | 0.021,0.86,0.010,6.42,24.1 | 3 | 2206
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0583 | 7.296e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.068 | ug/dscm | 5.83e-08 |  | 2 | 1192
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0261 | 3.273e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.0305 | ug/dscm | 2.61e-08 |  | 3 | 1192
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0281 | 3.519e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.0328 | ug/dscm | 2.81e-08 |  | 4 | 1192
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0316 | 3.745e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.0349 | ug/dscm | 3.16e-08 |  | 1 | 1195
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0261 | 3.09e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.0288 | ug/dscm | 2.61e-08 |  | 2 | 1195
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0357 | 4.238e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 0.0395 | ug/dscm | 3.57e-08 |  | 3 | 1195
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 1 |  | 0.109 | 0.0001309 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 119.0357 | ng/dscm | 1.0871e-07 | [ | 1 | 876
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 2 |  | 0.0969 | 0.0001163 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 105.7525 | ng/dscm | 9.6922e-08 | .0065, .474 | 2 | 876
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 3 | < | 0.0598 | 7.215e-05 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 65.5902 | ng/dscm | 5.9752e-08 | [<.308] | 3 | 876
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 1 |  | 0.0432 | 5.419e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 49.2623 | ng/dscm | 4.32e-08 | .006, [<.246] | 1 | 8761
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 2 |  | 0.0525 | 6.631e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 60.2859 | ng/dscm | 5.2477e-08 | .006, [<.327] | 2 | 8761
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 3 | < | 0.0402 | 5.053e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | BDL | BDL | 45.9321 | ng/dscm | 4.0218e-08 | [<.23] | 3 | 8761
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0632 | 8.563e-05 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 357057 | dscfm | 11.18 %H20, 14.69 %CO2, 4.79 %O2, 181 Deg F |  |  | DLL | DLL | 0.0798 | ug/dscm | 6.32e-08 |  | U00-M30B-R2 | 699
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0571 | 7.554e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 368805 | dscfm | 11.31 %H20, 14.36 %CO2, 5.15 %O2, 176 Deg F |  |  | DLL | DLL | 0.0704 | ug/dscm | 5.71e-08 |  | U00-M30B-R3 | 699
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0677 | 9.024e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 358184 | dscfm | 11.66 %H20, 14.34 %CO2, 5.11 %O2, 173 Deg F |  |  | DLL | DLL | 0.0841 | ug/dscm | 6.77e-08 |  | U00-M30B-R4 | 699
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 1.91 | 0.002507 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F |  |  | DLL | DLL | 2.336 | ug/dscm | 1.9085e-06 |  | 5 | 1146
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 7 |  | 1.66 | 0.002231 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F |  |  | DLL | DLL | 2.0791 | ug/dscm | 1.6605e-06 |  | 7 | 1146
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 6 |  | 1.82 | 0.002438 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F |  |  | DLL | DLL | 2.2725 | ug/dscm | 1.8227e-06 |  | 6 | 1146
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 1 |  | 7.7 | 0.01063 | mg/Nm3 | Unknown | 2010-03-29 | Refer to sample method | U.S. EPA Method 30B | 625992 | dscfm | 7.7 %H20, 15.54 %CO2, 3.76 %O2, 335.6 Deg F |  |  | ADL | ADL | 9.9036 | ug/dscm | 7.09e-06 |  | 1 | 1750
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 2 |  | 9.03 | 0.01245 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 628494 | dscfm | 8.3 %H20, 15.43 %CO2, 3.83 %O2, 335.5 Deg F |  |  | ADL | ADL | 11.605 | ug/dscm | 8.37e-06 |  | 2 | 1750
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 3 |  | 7.8 | 0.01076 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 629793 | dscfm | 8.3 %H20, 15.31 %CO2, 3.88 %O2, 334.9 Deg F |  |  | ADL | ADL | 10.0279 | ug/dscm | 7.28e-06 |  | 3 | 1750
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 5.93 | 0.006685 | mg/Nm3 | Unknown | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 1196818 | dscfm | 7.08 %H20, %CO2, %O2, 74 Deg F |  |  | ADL | ADL |  | ug/dscm | 3.25e-06 |  | Sample 1 | 829
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 6.69 | 0.007532 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 1202596 | dscfm | 6.92 %H20, 66 Deg F |  |  | ADL | ADL |  | ug/dscm | 3.66e-06 |  | Sample 2 | 829
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 7.86 | 0.008852 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 1197709 | dscfm | 6.52 %H20, %CO2, %O2, 76 Deg F |  |  | ADL | ADL |  | ug/dscm | 4.3e-06 |  | Sample 3 | 829
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 6.17 | 0.007718 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1278916 | dscfm | 12.45 %H20, 13.3 %CO2, 6.3 %O2, 376 Deg F |  |  | ADL | ADL | 7.193 | ug/dscm | 6.17e-06 |  | 3 | 900000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 4 |  | 6.33 | 0.007973 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1290170 | dscfm | 12.65 %H20, 13.5 %CO2, 6.2 %O2, 378 Deg F |  |  | ADL | ADL | 7.431 | ug/dscm | 6.33e-06 |  | 4 | 900000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 5 |  | 7.58 | 0.009551 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1283352 | dscfm | 10.01 %H20, 13.5 %CO2, 6.2 %O2, 392 Deg F |  |  | ADL | ADL | 8.901 | ug/dscm | 7.58e-06 |  | 5 | 900000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.773 | 0.001091 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 163426 | dscfm | 6.49 %H20, 14.72 %CO2, 4.28 %O2, 412 Deg F |  |  | ADL | ADL | 1.0171 | ug/dscm | 7.73e-07 |  | 1 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.879 | 0.001239 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 163351 | dscfm | 7.17 %H20, 14.79 %CO2, 4.1 %O2, 415 Deg F |  |  | ADL | ADL | 1.1544 | ug/dscm | 8.79e-07 |  | 2 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.922 | 0.001313 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B | 160792 | dscfm | 7.82 %H20, 14.77 %CO2, 4.1 %O2, 417 Deg F |  |  | ADL | ADL | 1.2237 | ug/dscm | 9.22e-07 |  | 3 | 1066
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 | UNK | 3.48 | 0.004755 | mg/Nm3 | Poor | 2010-07-13 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 4322.6974 | ng/dscm | 3.484e-06 |  | 1 | 2070
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 | UNK | 3.72 | 0.005115 | mg/Nm3 | Poor | 2010-07-13 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 4650.0407 | ng/dscm | 3.7243e-06 |  | 2 | 2070
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 | UNK | 3.59 | 0.004948 | mg/Nm3 | Poor | 2010-07-14 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported. |  |  | UNK | 4498.1013 | ng/dscm | 3.5935e-06 |  | 3 | 2070
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.24 | 0.002674 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1366625 | dscfm | 16.4 %H20, 14.9 %CO2, 5.2 %O2, 187 Deg F |  |  | ADL | ADL | 2.4925 | ug/dscm | 2.24e-06 |  | Run 1 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2 | 0.002406 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1362778 | dscfm | 16.6 %H20, 14.9 %CO2, 5.2 %O2, 185 Deg F |  |  | ADL | ADL | 2.2421 | ug/dscm | 2e-06 |  | Run 2 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.24 | 0.002674 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1366625 | dscfm | 16.4 %H20, 14.9 %CO2, 5.2 %O2, 187 Deg F |  |  | ADL | ADL | 2.4925 | ug/dscm | 2.24e-06 |  | Run 1 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2 | 0.002406 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1362778 | dscfm | 16.6 %H20, 14.9 %CO2, 5.2 %O2, 185 Deg F |  |  | ADL | ADL | 2.2421 | ug/dscm | 2e-06 |  | Run 2 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.42 | 0.002965 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1357797 | dscfm | 16.4 %H20, 15.1 %CO2, 5.1 %O2, 185 Deg F |  |  | ADL | ADL | 2.7629 | ug/dscm | 2.42e-06 |  | Run 3 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.42 | 0.002965 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1357797 | dscfm | 16.4 %H20, 15.1 %CO2, 5.1 %O2, 185 Deg F |  |  | ADL | ADL | 2.7629 | ug/dscm | 2.42e-06 |  | Run 3 | 1994
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.0996 | 0.0001374 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 1390000 | dscfm | 13.6 %H20, 14 %CO2, 5.2 %O2, 354 Deg F |  |  | ADL | ADL | 0.12805 | ug/dscm | 3.69e-06 |  | 2 | 1903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.106 | 0.0001458 | mg/Nm3 | Unknown | 2010-06-17 | Refer to sample method | U.S. EPA Method 30B | 1310000 | dscfm | 13.6 %H20, 13.9 %CO2, 4.8 %O2, 341 Deg F |  |  | ADL | ADL | 0.13589 | ug/dscm | 3.74e-06 |  | 3 | 1903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.106 | 0.0001466 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1310000 | dscfm | 14 %H20, 12.9 %CO2, 5.2 %O2, 347 Deg F |  |  | ADL | ADL | 0.13664 | ug/dscm | 3.74e-06 |  | 4 | 1903
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.00897 | 1.17e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 290557 | dscfm | 8.15 %H20, 14.5 %CO2, 5.43 %O2, 322.83 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.00623 | ug/dscm | 6.089e-09 |  | Run 1 | 1625
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0184 | 2.393e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 271693 | dscfm | 8.32 %H20, 15.3 %CO2, 5.4 %O2, 324.83 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0108 | ug/dscm | 9.251e-09 |  | Run 2 | 1625
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0179 | 2.328e-05 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 281639 | dscfm | 7.03 %H20, 15.7 %CO2, 5.36 %O2, 307.43 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0179 | ug/dscm | 1.585e-08 |  | Run 3 | 1625
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 1 |  | 0.00981 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B |  |  | 6.4 %H20, Deg F |  |  | ADL | ADL | 0.01 | ug/dscm | 9.81e-09 |  | 1 | 1312
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 2 |  | 0.00965 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B |  |  | 6.5 %H20, Deg F |  |  | ADL | ADL | 0.01 | ug/dscm | 9.65e-09 |  | 2 | 1312
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 3 |  | 0.0101 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 5.8 %H20, 11.4 %CO2, 7.8 %O2, Deg F |  |  | ADL | ADL | 0.01 | ug/dscm | 1.01e-08 |  | 3 | 1312
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 1 |  | 1.27 | 0.001556 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 1828760 | dscfm | 21.78 %H20, 13.41 %CO2, 6.21 %O2, 144 Deg F |  |  | ADL | ADL | 1.45 | ug/dscm | 1.27e-06 |  | 1 | 1644
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 0.924 | 0.001266 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1793768 | dscfm | 21.23 %H20, 15.16 %CO2, 4.47 %O2, 143 Deg F |  |  | ADL | ADL | 1.18 | ug/dscm | 9.24e-07 |  | 2 | 1644
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 1.14 | 0.001556 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1835111 | dscfm | 21.23 %H20, 15.08 %CO2, 4.51 %O2, 143 Deg F |  |  | ADL | ADL | 1.45 | ug/dscm | 1.14e-06 |  | 3 | 1644
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0434 | 4.989e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.96 %CO2, 6.37 %O2, 337.2 Deg F |  |  | ADL | ADL | 0.0465 | ug/dscm | 4.34e-08 |  | 1 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0473 | 5.365e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.94 %CO2, 6.4 %O2, 344.1 Deg F |  |  | ADL | ADL | 0.05 | ug/dscm | 4.73e-08 |  | 2 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0333 | 3.97e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.42 %H20, 14.01 %CO2, 6.32 %O2, 339.1 Deg F |  |  | ADL | ADL | 0.037 | ug/dscm | 3.33e-08 |  | 3 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0434 | 4.989e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.96 %CO2, 6.37 %O2, 337.2 Deg F |  |  | ADL | ADL | 0.0465 | ug/dscm | 4.34e-08 |  | 1 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0473 | 5.365e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.94 %CO2, 6.4 %O2, 344.1 Deg F |  |  | ADL | ADL | 0.05 | ug/dscm | 4.73e-08 |  | 2 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0333 | 3.97e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.42 %H20, 14.01 %CO2, 6.32 %O2, 339.1 Deg F |  |  | ADL | ADL | 0.037 | ug/dscm | 3.33e-08 |  | 3 | 2051
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.12 | 0.0001609 | mg/Nm3 | Unknown | 2010-06-02 | Refer to sample method | U.S. EPA Method 30B | 93746 | dscfm | 8.37 %H20, 15.47 %CO2, 4.64 %O2, 341.3 Deg F |  |  | ADL | ADL | 0.15 | ug/dscm | 1.2e-07 |  | 2 | 2089
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.118 | 0.0001609 | mg/Nm3 | Unknown | 2010-06-03 | Refer to sample method | U.S. EPA Method 30B | 91738 | dscfm | 9.05 %H20, 15.57 %CO2, 4.51 %O2, 342.6 Deg F |  |  | ADL | ADL | 0.15 | ug/dscm | 1.18e-07 |  | 3 | 2089
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.144 | 0.0001931 | mg/Nm3 | Unknown | 2010-06-01 | Refer to sample method | U.S. EPA Method 30B | 94701 | dscfm | 9 %H20, 15.42 %CO2, 4.56 %O2, 346.5 Deg F |  |  | ADL | ADL | 0.18 | ug/dscm | 1.44e-07 |  | 1 | 2089
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 1 |  | 1.21 | 0.001581 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1437.6749 | ng/dscm | 1.2147e-06 | Fraction 1B [ | M29-1 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 |  | 1.12 | 0.001456 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1323.973 | ng/dscm | 1.1164e-06 | Fraction 1B 0.017 ADL, Fraction 2B 1.93 ADL, Fraction 3A [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 |  | 1.2 | 0.001567 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1424.1328 | ng/dscm | 1.1993e-06 | Fraction 1B [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 1 |  | 1.21 | 0.001581 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1437.6749 | ng/dscm | 1.2147e-06 | Fraction 1B [ | M29-1 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 |  | 1.12 | 0.001456 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1323.973 | ng/dscm | 1.1164e-06 | Fraction 1B 0.017 ADL, Fraction 2B 1.93 ADL, Fraction 3A [ | M29-2 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 |  | 1.2 | 0.001567 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 1424.1328 | ng/dscm | 1.1993e-06 | Fraction 1B [ | M29-3 | 1176
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 0.373 | 0.0004335 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1627239 | dscfm | 120.52 Deg F |  |  | ADL | ADL | 0.404 | ug/dscm | 3.73e-07 |  | 1 | 1186
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 0.222 | 0.0002575 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1620043 | dscfm | 120.96 Deg F |  |  | ADL | ADL | 0.24 | ug/dscm | 2.22e-07 |  | 2 | 1186
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.255 | 0.0002983 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1640091 | dscfm | 120.33 Deg F |  |  | ADL | ADL | 0.278 | ug/dscm | 2.55e-07 |  | 3 | 1186
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 0.421 | 0.0005032 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1761667 | dscfm | 11.4 %H20, 120 Deg F |  |  | ADL | ADL | 0.469 | ug/dscm | 4.21e-07 |  | 2 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.515 | 0.0006148 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1761667 | dscfm | 11.4 %H20, 120 Deg F |  |  | ADL | ADL | 0.573 | ug/dscm | 5.15e-07 |  | 3 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 |  | 0.395 | 0.0004678 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1759587 | dscfm | 11.58 %H20, 120 Deg F |  |  | ADL | ADL | 0.436 | ug/dscm | 3.95e-07 |  | 4 | 1187
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 1 |  | 0.325 | 0.0003723 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 654237 | dscfm | 6.97 %H20, 11.86 %CO2, 7.28 %O2, 307.9 Deg F |  |  | ADL | ADL | 0.347 | ug/dscm | 3.25e-07 |  | 1 | 1603
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 3 |  | 0.326 | 0.0003745 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 650476 | dscfm | 7.18 %H20, 11.8 %CO2, 7.24 %O2, 311 Deg F |  |  | ADL | ADL | 0.349 | ug/dscm | 3.26e-07 |  | 3 | 1603
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 4 |  | 0.304 | 0.0003541 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 704425 | dscfm | 7.13 %H20, 11.98 %CO2, 7.07 %O2, 314.4 Deg F |  |  | ADL | ADL | 0.33 | ug/dscm | 3.04e-07 |  | 4 | 1603
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 2 |  | 0.47 | 0.0005386 | mg/Nm3 | Unknown | 2010-02-09 | Refer to sample method | U.S. EPA Method 30B | 702720 | dscfm | 6.4 %H20, 11.86 %CO2, 7.28 %O2, 315.5 Deg F |  |  | ADL | ADL | 0.502 | ug/dscm | 4.7e-07 |  | 2 | 1586
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 4 |  | 0.463 | 0.0005236 | mg/Nm3 | Unknown | 2010-02-12 | Refer to sample method | U.S. EPA Method 30B | 578620 | dscfm | 6.8 %H20, 11.8 %CO2, 7.24 %O2, 305.6 Deg F |  |  | ADL | ADL | 0.488 | ug/dscm | 4.63e-07 |  | 4 | 1586
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 5 |  | 0.508 | 0.0005891 | mg/Nm3 | Unknown | 2010-02-13 | Refer to sample method | U.S. EPA Method 30B | 699821 | dscfm | 5.94 %H20, 11.98 %CO2, 7.07 %O2, 313.5 Deg F |  |  | ADL | ADL | 0.549 | ug/dscm | 5.08e-07 |  | 5 | 1586
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 1 |  | 8.48 | 0.01137 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 10.6 | ug/dscm | 8.48e-06 |  | 1 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 2 |  | 5.66 | 0.007629 | mg/Nm3 | Unknown | 2010-04-07 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | ADL | ADL | 7.11 | ug/dscm | 5.66e-06 |  | 2 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 3 |  | 5.71 | 0.007361 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | DLL | DLL | 6.86 | ug/dscm | 5.71e-06 |  | 3 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 4 |  | 5.4 | 0.006964 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B | [5 empty] | DLL | DLL | 6.49 | ug/dscm | 5.4e-06 |  | 4 | 2106
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.82 | 0.00606 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 268362 | dscfm | 10.7 %H20, 11.8 %CO2, 8.2 %O2, 311 Deg F |  |  | ADL | ADL | 5.6478 | ug/dscm | 5.82e-06 |  | Run 1 | 2000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 4.31 | 0.004625 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 258116 | dscfm | 10.5 %H20, 11.3 %CO2, 8.8 %O2, 304 Deg F |  |  | ADL | ADL | 4.3102 | ug/dscm | 4.31e-06 |  | Run 3 | 2000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.69 | 0.003233 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 266685 | dscfm | 11.1 %H20, 12.4 %CO2, 7.7 %O2, 313 Deg F |  |  | ADL | ADL | 3.0129 | ug/dscm | 2.69e-06 |  | Run 2 | 2000
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1.33 | 0.001497 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1059520 | dscfm | 12.8 %CO2, 5.4 %O2, 285 Deg F |  |  | ADL | ADL | 1.3954 | ug/dscm | 1.33e-06 |  | 1A | 835
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1.06 | 0.001281 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1066226 | dscfm | 12.8 %CO2, 5.4 %O2, 294 Deg F |  |  | ADL | ADL | 1.1938 | ug/dscm | 1.06e-06 |  | 2A | 835
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1.29 | 0.001575 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1058820 | dscfm | 12.7 %CO2, 5 %O2, 287 Deg F |  |  | ADL | ADL | 1.4677 | ug/dscm | 1.29e-06 |  | 3A | 835
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.11 | 0.005075 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 550371 | dscfm | 12.9 %H20, 13.5 %CO2, 6.4 %O2, 200 Deg F |  |  | ADL | ADL | 4.73 | ug/dscm | 4.11e-06 |  | 1 | 950
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.88 | 0.007318 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 703316 | dscfm | 13.7 %H20, 13.2 %CO2, 6.13 %O2, 200 Deg F |  |  | ADL | ADL | 6.82 | ug/dscm | 5.88e-06 |  | 2 | 950
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 6.91 | 0.008573 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 719304 | dscfm | 12.8 %H20, 13.5 %CO2, 6.33 %O2, 204 Deg F |  |  | ADL | ADL | 7.99 | ug/dscm | 6.91e-06 |  | 3 | 950
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 6.01 | 0.008021 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 7291.3901 | ng/dscm | 6.0121e-06 | [ | 1 | 1058
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 14.6 | 0.01975 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | DLL | ADL | 17956.8366 | ng/dscm | 1.4619e-05 | 0.0153, 69.2, 0.379, 44.9, 11.5, lowest standard of the calibration curve | 2 | 1058
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 11.7 | 0.01558 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 29 | [5 empty] | DLL | ADL | 14166.9922 | ng/dscm | 1.1681e-05 | 0.175, 59.9, 0.380, 11.4, 29.0, lowest standard of the calibration curve | 3 | 1058
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 6.01 | 0.008021 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 7291.3901 | ng/dscm | 6.0121e-06 | [ | 1 | 1060
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 14.6 | 0.01975 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29 | [5 empty] | DLL | ADL | 17956.8366 | ng/dscm | 1.4619e-05 | 0.0153, 69.2, 0.379, 44.9, 11.5, lowest standard of the calibration curve | 2 | 1060
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 11.7 | 0.01558 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 29 | [5 empty] | DLL | ADL | 14166.9922 | ng/dscm | 1.1681e-05 | 0.175, 59.9, 0.380, 11.4, 29.0, lowest standard of the calibration curve | 3 | 1060
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.00952 | 9.657e-06 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 283691 | dscfm | 11.789 %H20, 10.843 %CO2, 8.819 %O2, 135.3 Deg F |  | Concentration 10X low. | ADL | ADL | 0.0009 | ug/dscm | 9.52e-09 |  | 1-Hg | 1973
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.017 | 1.824e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 279109 | dscfm | 11.8 %H20, 10.939 %CO2, 8.625 %O2, 136.9 Deg F |  |  | ADL | ADL | 0.017 | ug/dscm | 1.7e-08 |  | 2-Hg | 1973
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0337 | 3.541e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B | 282405 | dscfm | 11.5 %H20, 10.7 %CO2, 8.9 %O2, 137.4 Deg F |  |  | ADL | ADL | 0.033 | ug/dscm | 3.37e-08 |  | 4-Hg | 1973
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 1 |  | 10.1 | 0.01016 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 245984 | dscfm | 7.18 %H20, 9.6 %CO2, 9.6 %O2, 317 Deg F |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 9.4725 | ug/dscm | 1.01e-05 |  | 1 | 1907
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 2 |  | 9.16 | 0.00874 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 247799 | dscfm | 7.55 %H20, 9.9 %CO2, 9.4 %O2, 316 Deg F |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 8.1451 | ug/dscm | 9.16e-06 |  | 2 | 1907
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 3 |  | 10.9 | 0.01073 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 249097 | dscfm | 7.69 %H20, 10.1 %CO2, 9.2 %O2, 316 Deg F |  | Incorrect facility_id in EPA database. Changed from 7253 to 7286. | ADL | ADL | 9.9991 | ug/dscm | 1.09e-05 |  | 3 | 1907
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 5.77 | 0.006866 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 30B | 131488 | dscfm | 7.3 %H20, 12.65 %CO2, 6.76 %O2, 327.3 Deg F |  |  | DLL | DLL | [<6.399] | ug/dscm |  |  | 1 | 904002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 7.99 | 0.009517 | mg/Nm3 | Unknown | 2010-04-12 | Refer to sample method | U.S. EPA Method 30B | 132118 | dscfm | 7.2 %H20, 12.8 %CO2, 6.73 %O2, 323.7 Deg F |  |  | ADL | ADL | 8.8697 | ug/dscm | 7.9874e-06 |  | 2 | 904002
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 8.52 | 0.01002 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 128052 | dscfm | 6.91 %O2, 318 Deg F |  |  | ADL | ADL | 9.34 | ug/dscm | 8.52e-06 |  | 3 | 904001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.00643 | 7.511e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.2 %CO2, 7 %O2, 171 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.009 | ug/dscm | 8.23e-09 |  | Run 1 | 202301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.00551 | 6.438e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.1 %CO2, 7.5 %O2, 171 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0091 | ug/dscm | 8.64e-09 |  | Run 2 | 202301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.00441 | 5.15e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.1 %CO2, 7.6 %O2, 171 Deg F |  | Conversion error due to incorrect mass | ADL | ADL | 0.0051 | ug/dscm | 4.92e-09 |  | Run 3 | 202301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0167 | 1.878e-05 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.2 %CO2, 7.4 %O2 |  | Conversion error due to incorrect mass units used and converting to emission | ADL | ADL | 0.0169 | ug/dscm | 1.6e-08 |  | Run 1 | 202302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0124 | 1.395e-05 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %CO2, 7.5 %O2, Deg F |  | Conversion error due to incorrect mass units used and converting to emission | ADL | ADL | 0.0091 | ug/dscm | 8.7e-09 |  | Run 2 | 202302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.00571 | 6.438e-06 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.2 %CO2, 7.4 %O2 |  | Conversion error due to incorrect mass units used and converting to emission | ADL | ADL | 0.008 | ug/dscm | 7.58e-09 |  | Run 3 | 202302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.111 | 0.0001449 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 844209 | dscfm | 12.7 %H20, 13.796 %CO2, 5.434 %O2, 120.58333333 Deg F |  |  | ADL | ADL | 0.135 | ug/dscm | 1.1139e-07 |  | 1 | 984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.109 | 0.0001416 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 844209 | dscfm | 12.7 %H20, 13.796 %CO2, 5.434 %O2, 120.75 Deg F |  |  | ADL | ADL | 0.132 | ug/dscm | 1.0891e-07 |  | 2 | 984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.139 | 0.0001792 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 837533 | dscfm | 21.7 %H20, 13.693 %CO2, 5.525 %O2, 120.25 Deg F |  |  | ADL | ADL | 0.167 | ug/dscm | 1.386e-07 |  | 3 | 984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.115 | 0.0001491 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 837533 | dscfm | 12.6 %H20, 13.693 %CO2, 5.525 %O2, 120 Deg F |  |  | ADL | ADL | 0.139 | ug/dscm | 1.1537e-07 |  | 4 | 984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 5 |  | 0.173 | 0.000221 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 856761 | dscfm | 12.9 %H20, 13.585 %CO2, 5.672 %O2, 120.83333333 Deg F |  |  | ADL | ADL | 0.206 | ug/dscm | 1.7262e-07 |  | 5 | 984
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.15 | 0.0001985 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1434478 | dscfm | 13 %H20, 13.979 %CO2, 5.145 %O2, 121.91666667 Deg F |  |  | ADL | ADL | 0.185 | ug/dscm | 1.4984e-07 |  | 3 | 986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 0.185 | 0.0002457 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1434478 | dscfm | 13 %H20, 13.979 %CO2, 5.145 %O2, 121.5 Deg F |  |  | ADL | ADL | 0.229 | ug/dscm | 1.8548e-07 |  | 4 | 986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 0.124 | 0.0001642 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1482128 | dscfm | 12.9 %H20, 14.067 %CO2, 5.122 %O2, 120.75 Deg F |  |  | ADL | ADL | 0.153 | ug/dscm | 1.2374e-07 |  | 5 | 986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 6 |  | 0.142 | 0.0001878 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1482128 | dscfm | 13 %H20, 14.067 %CO2, 5.122 %O2, 121.75 Deg F |  |  | ADL | ADL | 0.175 | ug/dscm | 1.4154e-07 |  | 6 | 986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 7 |  | 0.154 | 0.0002039 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1419396 | dscfm | 12.9 %H20, 13.984 %CO2, 5.142 %O2, 121 Deg F |  |  | ADL | ADL | 0.19 | ug/dscm | 1.5386e-07 |  | 7 | 986
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 6.64 | 0.009153 | mg/Nm3 | Unknown | 2010-07-13 | Not Specified | EPA method 29 | [5 empty] | ADL | DLL | 8321.327 | ng/dscm | 6.6355e-06 | FH - BDL - 0.20 NON DETECT REPORTED AS LAB REPORTING LIMIT BH FRACTION 1 - ADL - 15.6 BLANK CORRECTED BH FRACTION 2 - ADL - 0.75 BLANK CORRECTED BH FRACTION 3 - BDL - 0.16 NON DETECT REPORTED AS LAB REPORTING LIMIT BH FRACTION 4 - ADL - 16.2 BLANK CORRECT | 1 | 2103
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 6.6 | 0.008987 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 | [5 empty] | ADL | DLL | 8170.1558 | ng/dscm | 6.5974e-06 | FH - BDL - 0.20 NON DETECT REPORTED AS LAB REPORTING LIMIT BH FRACTION 1 - ADL - 17.9 BLANK CORRECTED BH FRACTION 2 - ADL - 0.68 BLANK CORRECTED BH FRACTION 3 - ADL - 0.30 BLANK CORRECTED BH FRACTION 4 - ADL - 13.5 BLANK CORRECTED | 2 | 2103
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 8.57 | 0.01204 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 | [5 empty] | ADL | DLL | 10945.1158 | ng/dscm | 8.5671e-06 | FH - BDL - 0.20 NON DETECT REPORTED AS LAB REPORTING LIMIT BH FRACTION 1 - ADL - 22.6 BLANK CORRECTED BH FRACTION 2 - ADL - 0.82 BLANK CORRECTED BH FRACTION 3 - ADL - 0.060 BLANK CORRECTED BH FRACTION 4 - ADL - 19.6 BLANK CORRECTED | 3 | 2103
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 0.448 | 0.000503 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 152023 | dscfm | 8.42 %H20, 11.746 %CO2, 7.899 %O2, 296.6 Deg F | Results may be biased low due to matrix interference. |  | ADL | ADL | 0.46878 | ug/dscm | 4.4847e-07 |  | 1 | 1062
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 0.514 | 0.0005704 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 154852 | dscfm | 8.87 %H20, 11.61 %CO2, 8.052 %O2, 300.5 Deg F | Results may be biased low due to matrix interference. |  | ADL | ADL | 0.53157 | ug/dscm | 5.1449e-07 |  | 2 | 1062
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 0.232 | 0.0002844 | mg/Nm3 | Poor | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 142931 | dscfm | 9.24 %H20, 12.857 %CO2, 6.685 %O2, 289.1 Deg F | Results may be biased low due to matrix interference. RPD of >20% and spike recovery of 50% outside method limit of 85-115%. |  | ADL | ADL | 0.26504 | ug/dscm | 2.3164e-07 |  | 3 | 1062
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0925 | 0.0001137 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 940740 | dscfm | 11.32 %H20, 12.795373822 %CO2, 6.37 %O2, 120.1 Deg F |  | Missing flag |  | ADL | 0.106 | ug/dscm | 9.25e-08 |  | 2017-01-01 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0925 | 0.0001137 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 940740 | dscfm | 11.32 %H20, 12.795373822 %CO2, 6.37 %O2, 120.1 Deg F |  | Missing flag |  | ADL | 0.106 | ug/dscm | 9.25e-08 |  | 2017-01-02 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0923 | 0.000103 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 948006 | dscfm | 11.33 %H20, 12.830598526 %CO2, 6.33 %O2, 120.1 Deg F |  | Missing flag |  | ADL | 0.096 | ug/dscm | 9.23e-08 |  | 2017-02-01 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0923 | 0.0001223 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 948006 | dscfm | 11.33 %H20, 12.830598526 %CO2, 6.33 %O2, 120.1 Deg F |  | Missing flag |  | ADL | 0.114 | ug/dscm | 9.23e-08 |  | 2017-02-02 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0988 | 0.0001212 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 949743 | dscfm | 11.45 %H20, 12.82179235 %CO2, 6.34 %O2, 120.5 Deg F |  | Missing flag |  | ADL | 0.113 | ug/dscm | 2.079e-07 |  | 2017-03-01 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.108 | 0.0001331 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 949743 | dscfm | 11.45 %H20, 12.82179235 %CO2, 6.34 %O2, 120.5 Deg F |  | Missing flag |  | ADL | 0.124 | ug/dscm | 2.079e-07 |  | 2017-03-02 | 120301
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0672 | 7.683e-05 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 876652 | dscfm | 10.3 %H20, 12.936272639 %CO2, 6.21 %O2, 116.8 Deg F |  | Missing flag |  | ADL | 0.0716 | ug/dscm | 6.72e-08 |  | 2017-01-01 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0672 | 8.97e-05 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 876652 | dscfm | 10.3 %H20, 12.936272639 %CO2, 6.21 %O2, 116.8 Deg F |  | Missing flag |  | ADL | 0.0836 | ug/dscm | 6.72e-08 |  | 2017-01-02 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0564 | 6.535e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 884700 | dscfm | 10.3 %H20, 12.751342942 %CO2, 6.42 %O2, 116.6 Deg F |  | Missing flag |  | ADL | 0.0609 | ug/dscm | 5.64e-08 |  | 2017-02-01 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0725 | 8.906e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 884700 | dscfm | 10.3 %H20, 12.751342942 %CO2, 6.42 %O2, 116.6 Deg F |  | Missing flag |  | ADL | 0.083 | ug/dscm | 5.64e-08 |  | 2017-02-02 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0595 | 7.586e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 846533 | dscfm | 11.2 %H20, 12.680893533 %CO2, 6.5 %O2, 119.1 Deg F |  | Missing flag |  | ADL | 0.0707 | ug/dscm | 5.95e-08 |  | 2017-03-01 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0595 | 7.146e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 846533 | dscfm | 11.2 %H20, 12.680893533 %CO2, 6.5 %O2, 119.1 Deg F |  | Missing flag |  | ADL | 0.0666 | ug/dscm | 5.95e-08 |  | 2017-03-02 | 120302
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0607 | 7.618e-05 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1211393 | dscfm | 16.5 %H20, 13.4 %CO2, 5.9 %O2, 126 Deg F |  | Missing flag |  | ADL | 0.071 | ug/dscm | 6.07e-08 |  | 2017-01-01 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.045 | 5.687e-05 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1211393 | dscfm | 16.5 %H20, 13.4 %CO2, 5.9 %O2, 126 Deg F |  | Missing flag |  | ADL | 0.053 | ug/dscm | 4.5e-08 |  | 2017-01-02 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.03 | 3.756e-05 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 1157212 | dscfm | 13.5 %H20, 13.7 %CO2, 5.4 %O2, 119 Deg F |  | Missing flag |  | ADL | 0.035 | ug/dscm | 3e-08 |  | 2017-02-01 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.029 | 3.756e-05 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 1157212 | dscfm | 13.5 %H20, 13.7 %CO2, 5.4 %O2, 119 Deg F |  | Missing flag |  | ADL | 0.035 | ug/dscm | 2.9e-08 |  | 2017-02-02 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0717 | 9.228e-05 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1255382 | dscfm | 13.8 %H20, 13.6 %CO2, 5.5 %O2, 120 Deg F |  | Missing flag |  | ADL | 0.086 | ug/dscm | 7.17e-08 |  | 2017-03-01 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0665 | 8.584e-05 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1255382 | dscfm | 13.8 %H20, 13.6 %CO2, 5.5 %O2, 120 Deg F |  | Missing flag |  | ADL | 0.08 | ug/dscm | 6.65e-08 |  | 2017-03-02 | 120303
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0631 | 8.047e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.3 %H20, 13.5 %CO2, 5.7 %O2, 116 Deg F |  | Missing flag |  | ADL | 0.075 | ug/dscm | 6.31e-08 |  | 2017-01-01 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0684 | 8.691e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.3 %H20, 13.5 %CO2, 5.7 %O2, 116 Deg F |  | Missing flag |  | ADL | 0.081 | ug/dscm | 6.84e-08 |  | 2017-01-02 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0234 | 3.004e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.2 %H20, 13.5 %CO2, 5.7 %O2, 117 Deg F |  | Missing flag |  | ADL | 0.028 | ug/dscm | 2.34e-08 |  | 2017-02-01 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0249 | 3.219e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.2 %H20, 13.5 %CO2, 5.7 %O2, 117 Deg F |  | Missing flag |  | ADL | 0.03 | ug/dscm | 2.49e-08 |  | 2017-02-02 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0164 | 2.146e-05 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1131652 | dscfm | 12.1 %H20, 13.5 %CO2, 5.5 %O2, 115 Deg F |  | Missing flag |  | ADL | 0.02 | ug/dscm | 1.64e-08 |  | 2017-03-01 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0817 | 0.0001052 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1131652 | dscfm | 12.1 %H20, 13.5 %CO2, 5.5 %O2, 115 Deg F |  | Missing flag; conversion error due to incorrect mass |  | ADL | 0.021 | ug/dscm | 1.71e-08 |  | 2017-03-02 | 120304
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 2.73 | 0.003906 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B | 566768 | dscfm | 19.08 %H20, 15.8 %CO2, 3.76 %O2, 191 Deg F |  |  | ADL | ADL | 3.64 | ug/dscm | 2.73e-06 |  | 2 | 837
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 4.68 | 0.006728 | mg/Nm3 | Poor | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B | 582512 | dscfm | 17.55 %H20, 16.04 %CO2, 3.68 %O2, 192 Deg F | Spike recovery >115%; invalid run. |  | ADL | ADL | 6.27 | ug/dscm | 4.68e-06 |  | 3 | 837
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 3.83 | 0.005504 | mg/Nm3 | Unknown | 2010-03-03 | Refer to sample method | U.S. EPA Method 30B | 580652 | dscfm | 19.41 %H20, 16 %CO2, 3.67 %O2, 192 Deg F |  |  | ADL | ADL | 5.13 | ug/dscm | 3.83e-06 |  | 1 | 837
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 5.57 | 0.008176 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 579345 | dscfm | 19.67 %H20, 16.22 %CO2, 3.27 %O2, 192 Deg F |  |  | ADL | ADL | 7.62 | ug/dscm | 5.57e-06 |  | 1 | 832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 6.31 | 0.00926 | mg/Nm3 | Poor | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 563279 | dscfm | 20.47 %H20, 15.94 %CO2, 3.31 %O2, 194 Deg F | Spike recovery >115%; invalid run. |  | ADL | ADL | 8.63 | ug/dscm | 6.31e-06 |  | 2 | 832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 4.92 | 0.007178 | mg/Nm3 | Poor | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 580823 | dscfm | 19.76 %H20, 16.08 %CO2, 3.39 %O2, 193 Deg F | Spike recovery >115%; invalid run. |  | ADL | ADL | 6.69 | ug/dscm | 4.92e-06 |  | 3 | 832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.11 | 0.0008509 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 1.11e-06 |  | Sample 1 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 1.51 | 0.001159 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 1.51e-06 |  | Sample 2 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.837 | 0.0006417 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.37e-07 |  | Sample 3 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.11 | 0.0008509 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 1.11e-06 |  | Sample 1 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 1.51 | 0.001159 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 1.51e-06 |  | Sample 2 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.837 | 0.0006417 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration and flag missing |  | ADL |  | ug/dscm | 8.37e-07 |  | Sample 3 | 1082
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.0324 | 3.401e-05 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 242209 | dscfm | 4.9 %O2, 309 Deg F |  |  | ADL | ADL | 0.0317 | ug/dscm | 3.24e-08 |  | Run #1 | 1124
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0439 | 4.775e-05 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 247315 | dscfm | 5 %O2, 316 Deg F |  |  | ADL | ADL | 0.0445 | ug/dscm | 4.39e-08 |  | Run #2 | 1124
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0296 | 3.155e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 259777 | dscfm | 4.8 %O2, 305.9 Deg F |  |  | ADL | ADL | 0.0294 | ug/dscm | 2.96e-08 |  | Run #3 | 1124
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.00709 | 9.337e-06 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1327915 | dscfm | 11.37 %H20, 14.2 %CO2, 5.2 %O2, 185 Deg F |  | Conversion error | ADL | ADL | 0.0094 | ug/dscm | 7.66e-09 |  | 1A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.00602 | 7.833e-06 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1337687 | dscfm | 11.66 %H20, 14.3 %CO2, 5.2 %O2, 185 Deg F | Spiked trap invalid; results are only the unspiked trap |  | ADL | ADL | 0.0073 | ug/dscm | 6.02e-09 |  | 2A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.00642 | 7.956e-06 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1348413 | dscfm | 11.91 %H20, 14.5 %CO2, 5.9 %O2, 185 Deg F |  | Changed results to reflect average of unspiked and spike trap | ADL | ADL | 0.0062 | ug/dscm | 5.37e-09 |  | 3A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.00709 | 9.337e-06 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1327915 | dscfm | 11.37 %H20, 14.2 %CO2, 5.2 %O2, 185 Deg F |  | Changed results to reflect average of unspiked and spike trap | ADL | ADL | 0.0094 | ug/dscm | 7.66e-09 |  | 1A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.00602 | 7.833e-06 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1337687 | dscfm | 11.66 %H20, 14.3 %CO2, 5.2 %O2, 185 Deg F | Spiked trap invalid; results are only the unspiked trap |  | ADL | ADL | 0.0073 | ug/dscm | 6.02e-09 |  | 2A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.00642 | 7.956e-06 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1348413 | dscfm | 11.91 %H20, 14.5 %CO2, 5.9 %O2, 185 Deg F |  | Changed results to reflect average of unspiked and spike trap | ADL | ADL | 0.0062 | ug/dscm | 5.37e-09 |  | 3A | 527
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 28 | 0.0296 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 26913.5855 | ng/dscm | 2.7982e-05 | FH [<.081] | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 28.5 | 0.03025 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 27502.2032 | ng/dscm | 2.8522e-05 | FH [<.081] | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 33.3 | 0.03538 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 32161.9223 | ng/dscm | 3.3313e-05 | FH [<.081] | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 28 | 0.0296 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 26913.5855 | ng/dscm | 2.7982e-05 | FH [<.081] | 1 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 28.5 | 0.03025 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 27502.2032 | ng/dscm | 2.8522e-05 | FH [<.081] | 2 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 33.3 | 0.03538 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased. |  | DLL | DLL | 32161.9223 | ng/dscm | 3.3313e-05 | FH [<.081] | 3 | 1471
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 3.4 | 0.004822 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. |  | ADL | ADL | 4383.9972 | ng/dscm | 3.4029e-06 | 16.123, 0.015 | 1 | 1832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1.72 | 0.002578 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. Results biased low due to permanganate impinger being broken in transit to the lab. |  | ADL | ADL | 2343.4676 | ng/dscm | 1.7193e-06 | 8.643, 0.015 the permanganate impinger was broken in transit and could not be analyzed. Therefore, mercury results for run 2 are biased low. Broken lab fraction 3B (estimated) | 2 | 1832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 4.4 | 0.005915 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. |  | ADL | ADL | 5377.2102 | ng/dscm | 4.3981e-06 | 20.369, 0.021 | 3 | 1832
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 0.441 | 0.0005872 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. |  | ADL | ADL | 533.8425 | ng/dscm | 4.4096e-07 | 2.123, 0.015 (During the Sheldon Unit 2 test runs, the boiler experienced degrading performance due to pluggage. This condition lowers the quality of combustion, thus raising the percentage of carbon carryover in the flyash due to loss-of-ignition. This | 1 | 1833
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 0.326 | 0.000434 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. |  | ADL | ADL | 394.5579 | ng/dscm | 3.2591e-07 | 1.520, 0.015 (During the Sheldon Unit 2 test runs, the boiler experienced degrading performance due to pluggage. This condition lowers the quality of combustion, thus raising the percentage of carbon carryover in the flyash due to loss-of-ignition. This | 2 | 1833
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 0.225 | 0.0002672 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. |  | ADL | ADL | 242.9154 | ng/dscm | 2.2539e-07 | 0.934, 0.015 (During the Sheldon Unit 2 test runs, the boiler experienced degrading performance due to pluggage. This condition lowers the quality of combustion, thus raising the percentage of carbon carryover in the flyash due to loss-of-ignition. This | 3 | 1833
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F |  |  | ADL | ADL | 2.05 | ug/dscm | 1.48e-06 |  | 1 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.62 | ug/dscm | 1.18e-06 |  | 2 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.69 | ug/dscm | 1.23e-06 |  | 3 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F |  |  | ADL | ADL | 2.05 | ug/dscm | 1.48e-06 |  | 1 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.62 | ug/dscm | 1.18e-06 |  | 2 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.69 | ug/dscm | 1.23e-06 |  | 3 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F |  |  | ADL | ADL | 2.05 | ug/dscm | 1.48e-06 |  | 1 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.62 | ug/dscm | 1.18e-06 |  | 2 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F |  |  | ADL | ADL | 1.69 | ug/dscm | 1.23e-06 |  | 3 | 895
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.02 | 0.004964 | mg/Nm3 | Unknown | 2010-03-16 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 4513.0109 | ng/dscm | 5.016e-06 |  | 1 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 5.47 | 0.005368 | mg/Nm3 | Unknown | 2010-03-16 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 4880.4533 | ng/dscm | 5.4716e-06 |  | 2 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 4.8 | 0.004709 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 29 | [5 empty] | DLL | DLL | 4280.6024 | ng/dscm | 4.7991e-06 |  | 3 | 844
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 1 |  | 1.45 | 0.001931 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 839000 | dscfm | 11.8 %H20, 14.3 %CO2, 4.6 %O2, 315 Deg F |  |  | ADL | ADL | 1.8 | ug/dscm | 1.45e-06 |  | 1 | 1916
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 2 |  | 1.58 | 0.002114 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 839000 | dscfm | 11.8 %H20, 14.3 %CO2, 4.6 %O2, 315 Deg F |  |  | ADL | ADL | 1.97 | ug/dscm | 1.58e-06 |  | 2 | 1916
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 3 |  | 1.29 | 0.001728 | mg/Nm3 | Unknown | 2010-05-03 | Refer to sample method | U.S. EPA Method 30B | 850000 | dscfm | 12 %H20, 14 %CO2, 4.5 %O2, 318 Deg F |  |  | ADL | ADL | 1.61 | ug/dscm | 1.29e-06 |  | 3 | 1916
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 3.06 | 0.00353 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.4 %CO2, 9.5 %O2, 292.95 Deg F |  |  | ADL | ADL | 3.29 | ug/dscm | 3.06e-06 |  | 1 | 1025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 3.71 | 0.004292 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.3 %CO2, 9.6 %O2, 292.35 Deg F |  |  | ADL | ADL | 4 | ug/dscm | 3.71e-06 |  | 2 | 1025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.65 | 0.004217 | mg/Nm3 | Unknown | 2010-07-02 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.9 %CO2, 10 %O2, 300.45 Deg F |  |  | ADL | ADL | 3.93 | ug/dscm | 3.65e-06 |  | 3 | 1025
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.56 | 0.005429 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 6.7 %O2, 292.45 Deg F |  |  | ADL | ADL | 5.06 | ug/dscm | 4.56e-06 |  | 1 | 740
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 4.58 | 0.005451 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.7 %O2, 288.4 Deg F |  |  | ADL | ADL | 5.08 | ug/dscm | 4.58e-06 |  | 2 | 740
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.25 | 0.005022 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.8 %O2, 289.95 Deg F |  |  | ADL | ADL | 4.68 | ug/dscm | 4.25e-06 |  | 3 | 740
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 |  | 0.436 | 0.0005276 | mg/Nm3 | Poor | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 192592 | dscfm | 13.6899 %H20, 12.683 %CO2, 6.5 %O2, 189.52083333 Deg F | QC data outside method specified limits. High spike recovery |  | ADL | ADL | 0.49172 | ug/dscm | 4.3566e-07 |  | 1 | 719
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 |  | 0.261 | 0.0003266 | mg/Nm3 | Poor | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 182619 | dscfm | 13.4 %H20, 13.1 %CO2, 6.1 %O2, 187.25 Deg F | QC data outside method specified limits. High spike recovery |  | ADL | ADL | 0.30436 | ug/dscm | 2.6107e-07 |  | 2 | 719
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 |  | 0.142 | 0.0001788 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 184465 | dscfm | 13.7 %H20, 13.2 %CO2, 6 %O2, 186.20833333 Deg F |  |  | ADL | ADL | 0.16662 | ug/dscm | 1.4208e-07 |  | 3 | 719
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 2.97 | 0.003198 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 824382 | dscfm | 201.2 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 2.9704e-06 |  | Sample 1 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 3.16 | 0.003401 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 829622 | dscfm | 202.7 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.1644e-06 |  | Sample 2 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.18 | 0.003423 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 822115 | dscfm | 203.6 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.179e-06 |  | Sample 3 | 1136
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 2.57 | 0.002768 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 859716 | dscfm | 15 %H20, 188.7 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 2.57e-06 |  | Sample 1 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 4.21 | 0.004528 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 854084 | dscfm | 15.1 %H20, %CO2, %O2, 189 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 4.21e-06 |  | Sample 2 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.97 | 0.004271 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 846242 | dscfm | 15.3 %H20, %CO2, %O2, 189.3 Deg F |  | Concentration missing | ADL | ADL |  | ug/dscm | 3.97e-06 |  | Sample 3 | 1132
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 0.00145 | 2.146e-06 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 159508 | dscfm | 12.54 %H20, 14.03 %CO2, 4.89 %O2, 191 Deg F |  |  | ADL | ADL | 0.002 | ug/dscm | 1.45e-09 |  | 1 | 134702
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 |  | 0.00249 | 3.219e-06 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 156853 | dscfm | 12.53 %H20, 14.29 %CO2, 4.45 %O2, 193 Deg F |  |  | ADL | ADL | 0.003 | ug/dscm | 2.49e-09 |  | 2 | 134702
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 |  | 0.00396 | 5.365e-06 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 159616 | dscfm | 12.63 %H20, 13.7 %CO2, 4.97 %O2, 195 Deg F |  |  | ADL | ADL | 0.005 | ug/dscm | 3.96e-09 |  | 3 | 134702
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.705 | 0.0008852 | mg/Nm3 | Unknown | 2010-06-21 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 7.05e-07 |  | Sample 1 | 2078
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.666 | 0.0008359 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 6.66e-07 |  | Sample 2 | 2078
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.474 | 0.0005955 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B |  |  |  |  | Concentration missing | ADL | ADL |  | ug/dscm | 4.74e-07 |  | Sample 3 | 2078
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 9.31 | 0.01025 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 453327 | dscfm | 11.47 %H20, 11.53 %CO2, 7.96 %O2, 321.7 Deg F |  | Missing flag |  | ADL | 9.549 | ug/dscm | 9.3064e-06 |  | 1 | 2065
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 9.39 | 0.01104 | mg/Nm3 | Unknown | 2010-04-07 | Refer to sample method | U.S. EPA Method 30B | 447069 | dscfm | 11.45 %H20, 12.32 %CO2, 7.35 %O2, 307.8 Deg F |  | Missing flag |  | ADL | 10.292 | ug/dscm | 9.3873e-06 |  | 2 | 2065
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.42 | 0.005183 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B | 443559 | dscfm | 11.32 %H20, 12.29 %CO2, 7.2 %O2, 308.2 Deg F |  | Missing flag |  | ADL | 4.83 | ug/dscm | 4.4162e-06 |  | 3 | 2065
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 2.8 | 0.002859 | mg/Nm3 | Unknown | 2010-08-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.15 %O2, 291.75 Deg F |  |  | ADL | ADL | 2.6644 | ug/dscm | 2.8e-06 |  | 1 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 3.52 | 0.003681 | mg/Nm3 | Unknown | 2010-08-11 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.07 %O2, 295.33 Deg F |  |  | ADL | ADL | 3.4302 | ug/dscm | 3.52e-06 |  | 2 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 2.37 | 0.002477 | mg/Nm3 | Unknown | 2010-08-12 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.11 %O2, 286.31 Deg F |  |  | ADL | ADL | 2.3088 | ug/dscm | 2.37e-06 |  | 3 | 2308
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.0421 | 5.848e-05 | mg/Nm3 | Unknown | 2010-06-21 | Refer to sample method | U.S. EPA Method 30B | 151955 | dscfm | 8.87 %H20, 15.3 %CO2, 4.3 %O2, 315 Deg F |  |  | ADL | ADL | 0.0545 | ug/dscm | 3.68e-08 |  | 1 | 1945
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0623 | 8.648e-05 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 153420 | dscfm | 11.9 %H20, 15.6 %CO2, 4.3 %O2, 316 Deg F |  |  | ADL | ADL | 0.0806 | ug/dscm | 5.41e-08 |  | 2 | 1945
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0789 | 0.0001094 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 152310 | dscfm | 11.6 %H20, 14.9 %CO2, 4.5 %O2, 315 Deg F |  |  | ADL | ADL | 0.102 | ug/dscm | 6.87e-08 |  | 3 | 1945
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.83 | 0.00831 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 7554.2726 | ng/dscm | 5.8292e-06 | 25.499, 0.015 | 1 | 1735
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 6.52 | 0.01025 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 9321.2311 | ng/dscm | 6.5223e-06 | 32.942, 0.015 | 2 | 1735
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.8 | 0.007498 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 6816.2742 | ng/dscm | 4.8018e-06 | 24.106, 0.015 | 3 | 1735
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2.49 | 0.003437 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 3124.6454 | ng/dscm | 2.486e-06 | 9.998, 0.589 | 1 | 1734
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 3.42 | 0.0047 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 4272.6517 | ng/dscm | 3.4216e-06 | 14.483, 0.065 | 2 | 1734
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2.69 | 0.004139 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 3762.9738 | ng/dscm | 2.6899e-06 | 12.665, 0.156 | 3 | 1734
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 0.465 | 0.0006223 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1121239 | dscfm | 10 %H20, 14.2 %CO2, 5 %O2, 312.2 Deg F |  |  | ADL | ADL | 0.58 | ug/dscm | 4.0704e-07 |  | 2 | 1289004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 4 |  | 0.682 | 0.000912 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1119227 | dscfm | 11.6 %H20, 14.3 %CO2, 4.8 %O2, 313.5 Deg F |  |  | ADL | ADL | 0.85 | ug/dscm | 5.9352e-07 |  | 4 | 1289004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 5 |  | 1.17 | 0.001567 | mg/Nm3 | Unknown | 2010-05-28 | Refer to sample method | U.S. EPA Method 30B | 1111682 | dscfm | 11.1 %H20, 14 %CO2, 5.2 %O2, 307.9 Deg F |  |  | ADL | ADL | 1.46 | ug/dscm | 1.0282e-06 |  | 5 | 1289004
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1.23 | 0.001322 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 484727 | dscfm | 14.18 %H20, 13 %CO2, 5.98 %O2, 191 Deg F |  |  | ADL | ADL | 1.232 | ug/dscm | 1.23e-06 |  | 1 | 1573
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1.27 | 0.001347 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 483967 | dscfm | 14.18 %H20, 13 %CO2, 6.15 %O2, 191 Deg F |  |  | ADL | ADL | 1.255 | ug/dscm | 1.27e-06 |  | 2 | 1573
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.28 | 0.001361 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 482783 | dscfm | 14.17 %H20, 13.6 %CO2, 6.2 %O2, 191 Deg F |  |  | ADL | ADL | 1.268 | ug/dscm | 1.28e-06 |  | 3 | 1573
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.991 | 0.001221 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 1110.1821 | ng/dscm | 9.9051e-07 |  | 1 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.671 | 0.0008502 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 772.8713 | ng/dscm | 6.7079e-07 |  | 2 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.05 | 0.001319 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 1199.4269 | ng/dscm | 1.0481e-06 |  | 3 | 1568
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 10.1 | 0.01343 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29 | [5 empty] | DDL | DLL | 12210.2471 | ng/dscm | 1.0068e-05 | FH(ADL) = 0.11 BH Fraction 1 (ADL) = 31.4 BH Fraction 2 (ADL) = 10.2 BH Fraction 3 (BDL) = 0.16, laboratory reporting limit BH Fraction 4 (ADL) = 10.8 Blank Corrected | 1 | 941
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 7.16 | 0.01035 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 9404.9972 | ng/dscm | 7.1583e-06 | FH(ADL) = 0.18 BH Fraction 1 (ADL) = 30.3 BH Fraction 2 (ADL) = 0.59 BH Fraction 3 (ADL) = 0.12 BH Fraction 4 (ADL) = 10.0 Blank Corrected | 2 | 941
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 3.4 | 0.005035 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 4577.5278 | ng/dscm | 3.4035e-06 | FH(ADL) = 0.15 BH Fraction 1 (ADL) = 13.6 BH Fraction 2 (ADL) = 1.0 BH Fraction 3 (ADL) = 0.13 BH Fraction 4 (ADL) = 4.8 Blank Corrected | 3 | 941
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 1 |  | 4.51 | 0.005483 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 4984.7758 | ng/dscm | 4.5064e-06 |  | 1 | 1455
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 2 |  | 6.86 | 0.00833 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 7573.0687 | ng/dscm | 6.8598e-06 |  | 2 | 1455
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 3 |  | 5.06 | 0.006128 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 5571.2154 | ng/dscm | 5.0645e-06 |  | 3 | 1455
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0157 | 1.931e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.675 %CO2, 10.225 %O2, 332.075 Deg F |  |  | ADL | ADL | 0.018 | ug/dscm | 1.57e-08 |  | 1 | 1248
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0231 | 2.897e-05 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.225 %CO2, 10.675 %O2, 322.1 Deg F |  |  | ADL | ADL | 0.027 | ug/dscm | 2.31e-08 |  | 2 | 1248
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0191 | 2.361e-05 | mg/Nm3 | Unknown | 2010-07-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.3 %CO2, 10.6 %O2, 322.65 Deg F |  |  | ADL | ADL | 0.022 | ug/dscm | 1.91e-08 |  | 3 | 1248
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0382 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.2 %O2, 303.05 Deg F |  |  | ADL | ADL | 0.04 | ug/dscm | 3.82e-08 |  | 1 | 752
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0194 | 2.146e-05 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.2 %O2, 307.75 Deg F |  |  | ADL | ADL | 0.02 | ug/dscm | 1.94e-08 |  | 3 | 752
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0246 | 3.219e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.3 %O2, 311.15 Deg F |  |  | ADL | ADL | 0.03 | ug/dscm | 2.46e-08 |  | 4 | 752
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.031 | 4.292e-05 | mg/Nm3 | Unknown | 2010-04-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 5.9 %O2, 314.725 Deg F |  |  | ADL | ADL | 0.04 | ug/dscm | 3.1e-08 |  | 1 | 756
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.019 | 2.146e-05 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %CO2, 6 %O2, 311.6 Deg F |  |  | ADL | ADL | 0.02 | ug/dscm | 1.9e-08 |  | 2 | 756
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0128 | 1.073e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 5.9 %O2, 312.05 Deg F |  |  | ADL | ADL | 0.01 | ug/dscm | 1.28e-08 |  | 3 | 756
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0729 | 8.584e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.3 %CO2, 6.2 %O2, 311.2 Deg F |  |  | ADL | ADL | 0.08 | ug/dscm | 7.29e-08 |  | 1 | 760
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0491 | 6.438e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 5.9 %O2, 316.6 Deg F |  |  | ADL | ADL | 0.06 | ug/dscm | 4.91e-08 |  | 3 | 760
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0982 | 0.0001288 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.7 %CO2, 5.7 %O2, 319.85 Deg F |  |  | ADL | ADL | 0.12 | ug/dscm | 9.82e-08 |  | 4 | 760
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 72 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F |  |  | ADL | ADL | 0.564 | ug/dscm | 4.7e-07 |  | 1 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 72 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F |  |  | ADL | ADL | 0.386 | ug/dscm | 3.24e-07 |  | 3 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F |  |  | ADL | ADL | 0.564 | ug/dscm | 4.7e-07 |  | 1 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F |  |  | ADL | ADL | 0.386 | ug/dscm | 3.24e-07 |  | 3 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F |  |  | ADL | ADL | 0.564 | ug/dscm | 4.7e-07 |  | 1 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F |  |  | ADL | ADL | 0.386 | ug/dscm | 3.24e-07 |  | 3 | 1842
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.865 | 0.001014 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 3369921 | dscfm | 13.1 %H20, 12.26 %CO2, 6.96 %O2, 127 Deg F |  |  | DLL | DLL | [<0.945] | ug/dscm |  |  | 1 | 909
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1.4 | 0.001641 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3341205 | dscfm | 15 %H20, 12.23 %CO2, 6.93 %O2, 128 Deg F |  |  | DLL | DLL | [<1.529] | ug/dscm |  |  | 2 | 909
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.19 | 0.001399 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3346156 | dscfm | 14.9 %H20, 12.31 %CO2, 6.94 %O2, 129 Deg F |  |  | DLL | DLL | [<1.304] | ug/dscm |  |  | 3 | 909
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 5.25 | 0.004367 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 182545 | dscfm | 5.9 %H20, %CO2, %O2, 222 Deg F |  | Incorrect emission rate typed in; conversion error to concentration | ADL | ADL | 0.0047373 | ug/dscm | 5.52e-06 |  | Sample 1 | 980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 6.25 | 0.005204 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 186229 | dscfm | 6.3 %H20, %CO2, %O2, 213 Deg F |  | Incorrect emission rate typed in; conversion error to concentration | ADL | ADL | 0.0031135 | ug/dscm | 3.67e-06 |  | Sample 2 | 980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 3.94 | 0.003283 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 188034 | dscfm | 5.8 %H20, %CO2, %O2, 216 Deg F |  | Incorrect emission rate typed in; conversion error to concentration | ADL | ADL | 0.0032456 | ug/dscm | 3.81e-06 |  | Sample 3 | 980
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 1 |  | 6.5 | 0.007428 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1163199 | dscfm | 9 %H20, 11.5 %CO2, 7.3 %O2, 265.8 Deg F |  |  | ADL | ADL | 6.9231 | ug/dscm | 6.4957e-06 |  | 1 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 2 |  | 6.31 | 0.007169 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1204758 | dscfm | 8.75 %H20, 11.4 %CO2, 7.4 %O2, 275.1 Deg F |  |  | ADL | ADL | 6.6809 | ug/dscm | 6.3149e-06 |  | 2 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 3 |  | 6.32 | 0.007329 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1255300 | dscfm | 8.81 %H20, 11.9 %CO2, 7.1 %O2, 270.6 Deg F |  |  | ADL | ADL | 6.8307 | ug/dscm | 6.3161e-06 |  | 3 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 6.5 | 0.007428 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1163199 | dscfm | 9 %H20, 11.5 %CO2, 7.3 %O2, 265.8 Deg F |  |  | ADL | ADL | 6.9231 | ug/dscm | 6.4957e-06 |  | 1 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 6.31 | 0.007169 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1204758 | dscfm | 8.75 %H20, 11.4 %CO2, 7.4 %O2, 275.1 Deg F |  |  | ADL | ADL | 6.6809 | ug/dscm | 6.3149e-06 |  | 2 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 6.32 | 0.007329 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1255300 | dscfm | 8.81 %H20, 11.9 %CO2, 7.1 %O2, 270.6 Deg F |  |  | ADL | ADL | 6.8307 | ug/dscm | 6.3161e-06 |  | 3 | 1322
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 2.97 | 0.003848 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 3497.8571 | ng/dscm | 2.9675e-06 | 0.041,0.49,0.020,4.67,12.35 | 1 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 3.05 | 0.00388 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 3527.661 | ng/dscm | 3.0535e-06 | 0.041,0.5,0.014,0.22,14.83 | 2 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 2.79 | 0.00355 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 29 | [5 empty] | ADL | ADL | 3227.1449 | ng/dscm | 2.7934e-06 | 0.032,.0.48,0.0062,0.65,13.34 | 3 | 2207
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.369 | 0.0004077 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | U.S. EPA Method 30B | 807877 | dscfm | 12.1 %H20, 13.07 %CO2, 6.5 %O2, 338 Deg F |  |  | ADL | ADL | 0.38 | ug/dscm | 3.69e-07 |  | 1 | 2014
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.347 | 0.0003863 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B | 780068 | dscfm | 12.6 %H20, 13.23 %CO2, 6.2 %O2, 340.5 Deg F |  |  | ADL | ADL | 0.36 | ug/dscm | 3.47e-07 |  | 2 | 2014
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.391 | 0.0004399 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 798069 | dscfm | 12.9 %H20, 13.43 %CO2, 6 %O2, 348.8 Deg F |  |  | ADL | ADL | 0.41 | ug/dscm | 3.91e-07 |  | 3 | 2014
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 5.18 | 0.006213 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1437736 | dscfm | 10.2 %H20, 12.7 %CO2, 6.8 %O2, 306.3 Deg F |  |  | ADL | ADL | 5.79 | ug/dscm | 5.18e-06 |  | 1 | 1007001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 5.38 | 0.006138 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1513081 | dscfm | 11 %H20, 12.4 %CO2, 7.3 %O2, 299.4 Deg F |  |  | ADL | ADL | 5.72 | ug/dscm | 5.38e-06 |  | 2 | 1007001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.2 | 0.006052 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1517114 | dscfm | 10.8 %H20, 12.8 %CO2, 6.8 %O2, 298.6 Deg F |  |  | ADL | ADL | 5.64 | ug/dscm | 5.2e-06 |  | 3 | 1007001
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.38 | 0.001856 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 769000 | dscfm | 11.2 %H20, 13.8 %CO2, 5.3 %O2, 325 Deg F |  |  | DLL | DLL | 1.73 | ug/dscm | 1.38e-06 |  | 1 | 1608
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.956 | 0.001298 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 795000 | dscfm | 11.2 %H20, 14.1 %CO2, 5.1 %O2, 314 Deg F |  |  | DLL | DLL | 1.21 | ug/dscm | 9.56e-07 |  | 2 | 1608
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.638 | 0.0008723 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 769000 | dscfm | 11.2 %H20, 14.2 %CO2, 5 %O2, 310 Deg F |  |  | ADL | ADL | 0.813 | ug/dscm | 6.38e-07 |  | 3 | 1608
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1.08 | 0.001459 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1130576 | dscfm | 15.6 %H20, 13.8 %CO2, 5.51 %O2, 175.75 Deg F |  |  | DLL | DLL | 1.36 | ug/dscm | 1.08e-06 |  | 1 | 1616
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.839 | 0.001105 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 1132600 | dscfm | 15.7 %H20, 13.73 %CO2, 5.75 %O2, 178.87 Deg F |  |  | DLL | DLL | 1.03 | ug/dscm | 8.39e-07 |  | 2 | 1616
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.31 | 0.001719 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 1127753 | dscfm | 16 %H20, 13.76 %CO2, 5.57 %O2, 178.12 Deg F |  |  | DLL | DLL | 1.602 | ug/dscm | 1.31e-06 |  | 3 | 1616
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 8.87 | 0.01073 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 197956 | dscfm | 11.8 %H20, 13.8 %CO2, 6.16 %O2, 327 Deg F |  |  | ADL | ADL | 10 | ug/dscm | 8.87e-06 |  | 1 | 2105
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 9.45 | 0.01148 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 197944 | dscfm | 11.8 %H20, 13.8 %CO2, 6.16 %O2, 327 Deg F |  |  | ADL | ADL | 10.7 | ug/dscm | 9.45e-06 |  | 2 | 2105
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 7.98 | 0.009743 | mg/Nm3 | Unknown | 2010-03-25 | Refer to sample method | U.S. EPA Method 30B | 200131 | dscfm | 11.9 %H20, 13.9 %CO2, 6.08 %O2, 315 Deg F |  |  | ADL | ADL | 9.08 | ug/dscm | 7.98e-06 |  | 3 | 2105
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.04 | 0.001373 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1002207 | dscfm | 11.4 %H20, 14.3 %CO2, 5.3 %O2, 308.6 Deg F |  |  | ADL | ADL | 1.28 | ug/dscm | 9.13e-07 |  | 1 | 2012
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1.18 | 0.001567 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 1007312 | dscfm | 10.4 %H20, 14.5 %CO2, 5.1 %O2, 311.4 Deg F |  |  | ADL | ADL | 1.46 | ug/dscm | 1.18e-06 |  | 2 | 2012
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1.25 | 0.001652 | mg/Nm3 | Unknown | 2010-07-02 | Refer to sample method | U.S. EPA Method 30B | 972834 | dscfm | 11.8 %H20, 14.2 %CO2, 5.2 %O2, 311.5 Deg F |  |  | ADL | ADL | 1.54 | ug/dscm | 1.11e-06 |  | 3 | 2012
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 4.26 | 0.005633 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 238050 | dscfm | 15.1 %H20, 15.5 %CO2, 3.8 %O2, 184 Deg F |  | Conversion error due to incorrect mass units used and converting to emission | ADL | ADL | 5.68 | ug/dscm | 4.26e-06 |  | 1 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 5.06 | 0.006299 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 223103 | dscfm | 17.3 %H20, 15.7 %CO2, 3.7 %O2, 186 Deg F |  |  | ADL | ADL | 5.87 | ug/dscm | 4.38e-06 |  | 2 | 1490
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.38 | 0.007436 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 248616 | dscfm | 15.1 %H20, 15.3 %CO2, 4.4 %O2, 182 Deg F |  |  | ADL | ADL | 6.93 | ug/dscm | 5.38e-06 |  | 1 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 6.03 | 0.008326 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 240230 | dscfm | 16.5 %H20, 14.4 %CO2, 4.4 %O2, 180 Deg F |  |  | ADL | ADL | 7.76 | ug/dscm | 6.03e-06 |  | 2 | 1160
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 6.33 | 0.008745 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 227964 | dscfm | 17.1 %H20, 15 %CO2, 4.4 %O2, 180 Deg F |  |  | ADL | ADL | 8.15 | ug/dscm | 6.33e-06 |  | 3 | 1160

## data
Citation | Data Source | Unit Name | Control Devices | Power System | Gross Rated Power (MW) | Test Output (MW) | Operating Utility | Fuel Type | USGS Province | Fuel Source | Boiler Type | Power System Comments | Run Number | Detection Flag | Emission Factor (lb/trillion Btu) | Concentration | Concentration Units | Data Quality Rating | Sample Date | Analytical Method | Sampling Method | Stack Flow Rate | Stack Flow Rate Units | Stream Conditions | Concentration Comments
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.299 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 603270 | dscfm | 14 %H20, 12.2 %CO2, 6.4 %O2, 127.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.305 | 0.0003755 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 604361 | dscfm | 14 %H20, 12.3 %CO2, 6.4 %O2, 127.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_1Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.306 | 0.0003755 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 610789 | dscfm | 14.6 %H20, 12.3 %CO2, 6.2 %O2, 127.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_2Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.301 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 603270 | dscfm | 14 %H20, 12.2 %CO2, 6.4 %O2, 127.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_2Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.324 | 0.000397 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 604361 | dscfm | 14 %H20, 12.3 %CO2, 6.4 %O2, 127.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | A. B. Brown Generating Station 6137_2Config | NOx: SCR, PM: FFp, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 265 |  | Southern Indiana Gas and Electric Company | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.295 | 0.0003648 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 610789 | dscfm | 14.6 %H20, 12.3 %CO2, 6.2 %O2, 127.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 | < | 0.0301 | 4.017e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 235633 | dscfm | 9.3340627011 %H20, 14.393731406 %CO2, 5.2448223713 %O2, 274.83333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 | < | 0.0284 | 3.858e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 237651 | dscfm | 9.3410276982 %H20, 14.404474131 %CO2, 5.2738044833 %O2, 273.86666667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 | < | 0.00975 | 1.288e-05 | mg/Nm3 | Unknown | 2010-04-04 | Refer to sample method | U.S. EPA Method 30B | 238259 | dscfm | 9.4 %H20, 14.5 %CO2, 5.2 %O2, 272.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 1 | < | 0.0301 | 3.219e-05 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 246537 | dscfm | 9.3464218753 %H20, 12.909443402 %CO2, 6.93720472 %O2, 734.52333333 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 2 | < | 0.244 | 0.0003219 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 249027 | dscfm | 9.0331626568 %H20, 12.895945323 %CO2, 6.9703094476 %O2, 733.55666667 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Hawaii 10673_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 203 |  | AES Hawaii, Inc. | bituminous | Unknown | Columbia, Venezuela, Indonesia | Fluidized bed |  | 3 | < | 0.268 | 0.0003541 | mg/Nm3 | Unknown | 2010-04-03 | Refer to sample method | U.S. EPA Method 30B | 255597 | dscfm | 9.0200116335 %H20, 11.980561103 %CO2, 7.9318876933 %O2, 731.99 Deg F | Possible errors in OTM spreadsheet but insufficient docket data to confirm.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 |  | 1.31 | 0.001717 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 593113 | dscfm | 13 %H20, 12.5 %CO2, 6 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 |  | 1.32 | 0.001642 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 579657 | dscfm | 13.1 %H20, 12.3 %CO2, 6.8 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 |  | 1.36 | 0.001706 | mg/Nm3 | Unknown | 2010-03-08 | Refer to sample method | U.S. EPA Method 30B | 585852 | dscfm | 12.8 %H20, 12.7 %CO2, 6.1 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 1 |  | 2.02 | 0.002554 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 590544 | dscfm | 13.9 %H20, 13.3 %CO2, 5.6 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 2 |  | 2.2 | 0.002833 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 618616 | dscfm | 11.9 %H20, 12.7 %CO2, 6.1333333333 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Puerto Rico Cogeneration Facility 68029_Unit_2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDsd | Coal-Fired Boilers | 255 |  | AES Puerto Rico, L.P. | bituminous | Unknown | Unknown | Fluidized bed |  | 3 |  | 2.18 | 0.002704 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 594930 | dscfm | 13.6 %H20, 13.4 %CO2, 5.7333333333 %O2, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 0.0375 | 4.834e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 717418 | dscfm | 12.5 %H20, 15.559967101 %CO2, 3.9 %O2, 330 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 0.045 | 6.152e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 728890 | dscfm | 12.2 %H20, 15.523241735 %CO2, 3.9 %O2, 334 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 0.0332 | 4.713e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 732026 | dscfm | 12 %H20, 15.430807294 %CO2, 4 %O2, 335 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 1 |  | 0.0375 | 4.834e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 717418 | dscfm | 12.5 %H20, 15.559967101 %CO2, 3.9 %O2, 330 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 2 |  | 0.045 | 6.152e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 728890 | dscfm | 12.2 %H20, 15.523241735 %CO2, 3.9 %O2, 334 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Shady Point,LLC 10671_Unit 2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 284 |  | AES Corporation | subbit/bit | Northern Great Plains, Interior(West) | Powder River Basin, OK | Fluidized bed |  | 3 |  | 0.0332 | 4.713e-05 | mg/Nm3 | Poor | 2010-06-05 | Refer to sample method | U.S. EPA Method 30B | 732026 | dscfm | 12 %H20, 15.430807294 %CO2, 4 %O2, 335 Deg F | Third bed spike (50ng) much greater than that of the actual sample (2-5ng). Breakthrough to bed 2 was greater than 20% . The RPD was greater than 20%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 1 |  | 0.0311 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 406667 | dscfm | 6.6 %H20, 14.2 %CO2, 4.5 %O2, 286 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 3 |  | 0.0156 | 2.146e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 401885 | dscfm | 6.4 %H20, 15.3 %CO2, 4.2 %O2, 288 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | AES Warrior Run Cogeneration Facility 10678_BLR1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 202 |  | AES Warrior Run Limited Partnership | bituminous | Eastern | MD, WV | Fluidized bed |  | 4 |  | 0.0311 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-27 | Refer to sample method | U.S. EPA Method 30B | 404879 | dscfm | 6.3 %H20, 15.6 %CO2, 4.5 %O2, 297 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 11.1 | 0.01271 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 216648 | dscfm | 6.42 %H20, 11.79 %CO2, 7.3 %O2, 337 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 11.3 | 0.01314 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 212771 | dscfm | 6.2 %H20, 11.7 %CO2, 7.15 %O2, 341 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 12 | 0.01391 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 207564 | dscfm | 6.24 %H20, 11.96 %CO2, 7.19 %O2, 337 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 1 |  | 9.8 | 0.01141 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219193 | dscfm | 6.28 %H20, 12.52 %CO2, 6.98 %O2, 320.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 2 |  | 10.1 | 0.01187 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219502 | dscfm | 6.18 %H20, 12.45 %CO2, 6.8 %O2, 321.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Albright Power Station 3942_Unit_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Monongahela Power Company | bituminous | Eastern | PA, WV | Wall-fired |  | 3 |  | 8.85 | 0.01035 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 219900 | dscfm | 6.26 %H20, 12.35 %CO2, 6.91 %O2, 323.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.676 | 0.0008473 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 508239 | dscfm | 12.9 %H20, 12.1 %CO2, 6.2 %O2, 73 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.633 | 0.0008005 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 506246 | dscfm | 12.9 %H20, 12.2 %CO2, 6.1 %O2, 78 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_1d | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 207 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 5 |  | 0.702 | 0.0008816 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 506195 | dscfm | 12.9 %H20, 12.3 %CO2, 5.9 %O2, 81 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.24 | 0.001633 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 510586 | dscfm | 12.6 %H20, 12.8 %CO2, 5.4 %O2, 126 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 1.09 | 0.001424 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 501186 | dscfm | 13.5 %H20, 12.6 %CO2, 5.6 %O2, 125 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Asheville Steam Electric Plant 2706_Ash_Cfg_2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray,Forced ox), SO3: SI | Coal-Fired Boilers | 204 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 5 |  | 1.5 | 0.001966 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 504970 | dscfm | 12.8 %H20, 12.8 %CO2, 5.5 %O2, 125 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 5.13 | 0.006653 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 4.66 | 0.006024 | mg/Nm3 | Unknown | 2010-04-28 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Big Stone 6098_001 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 495 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 6.81 | 0.008613 | mg/Nm3 | Unknown | 2010-04-29 | Not Specified | EPA method 29 |  |  |  | Sampled at too high of a temperature
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 1 | < | 0.0128 | 1.623e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 2 | < | 0.0139 | 1.746e-05 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Birchwood Power Facility 54304_1A | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 222 |  | Birchwood Power Partners, L.P. | bituminous | Eastern | KY,WV | Tangential |  | 3 | < | 0.0197 | 2.49e-05 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.117 | 0.000162 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 864027 | dscfm | 11.93 %H20, 15.21 %CO2, 4.39 %O2, 289.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.122 | 0.0001695 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 864027 | dscfm | 11.93 %H20, 15.21 %CO2, 4.39 %O2, 289.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Bridgeport Station 568_BHSEMU3OS3-#2 | NOx: Unspecified, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 403 |  | PSEG Power, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.126 | 0.0001738 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 865350 | dscfm | 12.29 %H20, 15.22 %CO2, 4.45 %O2, 290.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.284 | 0.0003541 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 140597 | dscfm | 8.04 %H20, 13.9 %CO2, 5.91 %O2, 364 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.266 | 0.0003326 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 137425 | dscfm | 8.56 %H20, 13.86 %CO2, 5.89 %O2, 366.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.24 | 0.0003004 | mg/Nm3 | Unknown | 2010-05-14 | Refer to sample method | U.S. EPA Method 30B | 138430 | dscfm | 8.94 %H20, 13.87 %CO2, 5.86 %O2, 368.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.292 | 0.000397 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 135786 | dscfm | 6.56 %H20, 15.23 %CO2, 4.91 %O2, 372 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.284 | 0.0003755 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 135830 | dscfm | 6.57 %H20, 15.07 %CO2, 4.89 %O2, 372.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cambria Cogen 10641_002 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 49 |  | Northern Star Generation Services Company LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.279 | 0.0003755 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 134834 | dscfm | 7.12 %H20, 14.81 %CO2, 4.91 %O2, 373.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 1 |  | 0.0148 | 1.679e-05 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 |  |  |  | .0175, [
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 2 |  | 0.0536 | 6.049e-05 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Canadys Steam 3280_CAN003 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 185 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Wall-fired |  | 3 |  | 0.0618 | 6.914e-05 | mg/Nm3 | Unknown | 2010-05-13 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 2.97 | 0.003744 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 2.52 | 0.003157 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR4 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 168 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 2.38 | 0.002949 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 1.45 | 0.001881 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 1.62 | 0.002075 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cane Run 1363_CR5 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 181 |  | Louisville Gas & Electric Company | bituminous | Interior(East, North) | IL, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 1.86 | 0.002422 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 3.33 | 0.00418 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 338821 | dscfm | 7.1 %H20, 13.259 %CO2, 5.948 %O2, 273.33333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 2.88 | 0.003616 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 338821 | dscfm | 7.1 %H20, 13.259 %CO2, 5.948 %O2, 277.58333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 2.22 | 0.002798 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 338082 | dscfm | 7.2 %H20, 13.235 %CO2, 5.93 %O2, 273.58333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 2.41 | 0.003032 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 338082 | dscfm | 7.2 %H20, 13.235 %CO2, 5.93 %O2, 280.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cape Fear Steam Electric Plant 2708_Cap_Cfg_5b | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 153 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 4.66 | 0.005832 | mg/Nm3 | Unknown | 2010-03-25 | Refer to sample method | U.S. EPA Method 30B | 339979 | dscfm | 8.3 %H20, 13.404 %CO2, 6.029 %O2, 272.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 10.4 | 0.01013 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 1840874 | dscfm | 6 %H20, 11 %CO2, 8.3 %O2, 289 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 7.21 | 0.008713 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1834426 | dscfm | 63.8 %H20, 11 %CO2, 8.3 %O2, 282.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cardinal 2828_CD-U3 | NOx: SCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 650 |  | Cardinal Operating Company | bituminous | Eastern | KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.29 | 0.00662 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1719505 | dscfm | 10.1 %H20, 11.1 %CO2, 8.3 %O2, 299.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0259 | 4.569e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 254273 | dscfm | 6.7 %H20, 13.7 %CO2, 4.96 %O2, 338 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0152 | 2.678e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 257589 | dscfm | 10 %H20, 13.4 %CO2, 5.09 %O2, 336 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBA1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0256 | 4.503e-05 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 253299 | dscfm | 9.6 %H20, 13.5 %CO2, 5.27 %O2, 332 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0183 | 3.219e-05 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 275612 | dscfm | 13.6 %CO2, %O2, 324 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0206 | 3.627e-05 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 277164 | dscfm | 13.7 %CO2, 324 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBB1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0182 | 3.207e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 269532 | dscfm | 13.8 %CO2, %O2, 318 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 1 |  | 0.0284 | 5.457e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 246293 | dscfm | 12.7 %CO2, 5.8 %O2, 329 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 2 |  | 0.0239 | 4.218e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 247170 | dscfm | 13 %CO2, 5.7 %O2, 332 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cedar Bay Generating Company L.P. 10672_CBC1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 280 |  | Cedar Bay Generating Company L.P. | bituminous | Eastern | KY | Fluidized bed |  | 3 |  | 0.0271 | 4.262e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 246467 | dscfm | 13.1 %CO2, 5.6 %O2, 331 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 0.016 | 2.135e-05 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 336511 | dscfm | 11.92 %H20, 14.7 %CO2, 5.34 %O2, 180.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0235 | 3.122e-05 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 310424 | dscfm | 12.34 %H20, 14.11 %CO2, 5.43 %O2, 181.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 1 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0184 | 2.457e-05 | mg/Nm3 | Unknown | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 311350 | dscfm | 11.76 %H20, 13.75 %CO2, 5.34 %O2, 178.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0359 | 4.775e-05 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 318031 | dscfm | 13.19 %H20, 14.58 %CO2, 5.24 %O2, 179.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0279 | 2.479e-05 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 322994 | dscfm | 12.91 %H20, 14.99 %CO2, 4.79 %O2, 178.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Chambers Cogeneration LP 10566_Boil 2 | NOx: SCR, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Chambers Cogeneration LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0376 | 3.337e-05 | mg/Nm3 | Unknown | 2010-03-12 | Refer to sample method | U.S. EPA Method 30B | 323103 | dscfm | 12.99 %H20, 14.58 %CO2, 5.29 %O2, 179.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 |  | 3.13 | 0.004271 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 662681 | dscfm | 14.4 %H20, 15.02 %CO2, 4.65 %O2, 120.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 |  | 3.19 | 0.004405 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 662142 | dscfm | 14.5 %H20, 14.88 %CO2, 4.48 %O2, 121 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_003 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray) | Coal-Fired Boilers | 305 |  | Arizona Public Service | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 |  | 3.52 | 0.004839 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 660266 | dscfm | 14.7 %H20, 15.5 %CO2, 4.54 %O2, 121.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 1 |  | 1.44 | 0.00191 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 849901 | dscfm | 15.5 %H20, 16.47 %CO2, 5.18 %O2, 123.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 2 |  | 1.73 | 0.002285 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 855052 | dscfm | 15.4 %H20, 14.88 %CO2, 5.2 %O2, 123.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cholla 113_004 | NOx: Unspecified, PM: FF, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 425 |  | PacifiCorp | bituminous | Rocky Mountain | San Juan (NM) | Tangential |  | 3 |  | 2.02 | 0.002672 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 840622 | dscfm | 15.2 %H20, 15.75 %CO2, 5.15 %O2, 122.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 1 |  | 0.34 | 0.0004077 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1046703 | dscfm | 5.2 %H20, 6.6 %CO2, 13.4 %O2, 198 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 2 | < | 0.202 | 0.0002468 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 993033 | dscfm | 12.5 %H20, 6.5 %CO2, 13.4 %O2, 200.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 3 | < | 0.141 | 0.0001717 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 503173 | dscfm | 8.9 %H20, 13.8 %CO2, 4.9 %O2, 313.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clinch River 3775_CR-1 | NOx: SNCR, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 230 |  | Appalachian Power Company | bituminous | Eastern | VA | Vertical-fired |  | 4 | < | 0.226 | 0.0003112 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 495017 | dscfm | 8.4 %H20, 13.9 %CO2, 4.7 %O2, 305.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0202 | 2.468e-05 | mg/Nm3 | Unknown | 2010-03-29 | Refer to sample method | U.S. EPA Method 30B | 1070269 | dscfm | 13.27 %H20, 12.777 %CO2, 6.212 %O2, 124.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.0149 | 1.931e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 1043417 | dscfm | 12.97 %H20, 13.603 %CO2, 5.37 %O2, 122.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 431 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0256 | 3.219e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 1085103 | dscfm | 12.87 %H20, 13.167 %CO2, 6.02 %O2, 122.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0256 | 2.897e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 1120748 | dscfm | 12.89 %H20, 11.862175 %CO2, 6 %O2, 127.83585 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.0326 | 3.756e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 1079195 | dscfm | 12.85 %H20, 12.0636 %CO2, 6 %O2, 128.56852 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Clover 7213_Unit 2 | NOx: SNCR, PM: FFr, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 434 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0881 | 9.979e-05 | mg/Nm3 | Unknown | 2010-04-02 | Refer to sample method | U.S. EPA Method 30B | 1058382 | dscfm | 13.64 %H20, 11.8676 %CO2, 6 %O2, 130.42712 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.81 | 0.000882 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.71 %H20, 11.59 %CO2, 7.95 %O2, 372 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.7 | 0.0007414 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.96 %H20, 11.3 %CO2, 8.26 %O2, 376 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.423 | 0.0004635 | mg/Nm3 | Unknown | 2010-05-27 | Refer to sample method | U.S. EPA Method 30B |  |  | 9.41 %H20, 11.59 %CO2, 7.87 %O2, 372 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.358 | 0.0003595 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 481133 | dscfm | 7.8 %H20, 10.67 %CO2, 8.95 %O2, 310.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.577 | 0.0005901 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 477212 | dscfm | 7.6 %H20, 10.85 %CO2, 8.73 %O2, 303.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colbert 47_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 200 |  | Tennessee Valley Authority | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Rocky Mountain(Colorado, Utah) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.518 | 0.0005226 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 467926 | dscfm | 8.4 %H20, 10.72 %CO2, 8.91 %O2, 304.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.18 | 0.001437 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B | 1851508 | dscfm | 16 %H20, 13.063 %CO2, 6.569 %O2, 198.91666667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.971 | 0.001196 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1918056 | dscfm | 15.5 %H20, 13.159 %CO2, 6.493 %O2, 193.08333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colstrip 6076_Unit3 | NOx: Unspecified, PM: PS, SO2: FGDw(Venturi,Natural), Hg: ACSI | Coal-Fired Boilers | 805 |  | PPL Montana | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1 | 0.001214 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1911626 | dscfm | 16.5 %H20, 12.97 %CO2, 6.72 %O2, 192.54166667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.072 | 9.174e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 278182 | dscfm | 7.53 %H20, 14.91 %CO2, 4.91 %O2, 321.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.0709 | 8.96e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 278977 | dscfm | 7.26 %H20, 14.8 %CO2, 5.04 %O2, 321.26 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Colver Power Project 10143_AAB01 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 131 |  | Inter-Power/AhlCon Partners, L.P. | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.0719 | 9.228e-05 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B | 260530 | dscfm | 7.94 %H20, 14.89 %CO2, 4.92 %O2, 321.81 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 0.351 | 0.0004389 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 887000 | dscfm | 13.4 %H20, %CO2, 174 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 0.859 | 0.001073 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 920000 | dscfm | 13.3 %H20, 178 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Comanche 470_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 365 |  | Public Service Company of Colorado | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 0.254 | 0.0003176 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 827000 | dscfm | 12.2 %H20, %CO2, 171 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 2 |  | 11.7 | 0.01163 | mg/Nm3 | Unknown | 2010-06-28 | Refer to sample method | U.S. EPA Method 30B | 474066 | dscfm | 28.5 %H20, 10.7 %CO2, 9 %O2, 285.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 3 |  | 12.1 | 0.01189 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 391610 | dscfm | 27.8 %H20, 10.3 %CO2, 9.1 %O2, 278.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Conesville 2840_CV-3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 165 |  | Columbus Southern Power Company | bituminous | Eastern | WV, OH | Wall-fired | Front wall-fired boiler. | 5 |  | 11.1 | 0.01096 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 398635 | dscfm | 27.7 %H20, 10.4 %CO2, 9.1 %O2, 277.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.73 | 0.0008609 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.68 | 0.0008172 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC1-Conf | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 274 |  | Consumers Energy Co, et.al | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.654 | 0.0008041 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.73 | 0.0008609 | mg/Nm3 | Unknown | 2010-06-02 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.68 | 0.0008172 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Consumers Energy - J.H. Campbell 1710_JHC2-Conf | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 374 |  | Consumers Energy Co, et.al | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.654 | 0.0008041 | mg/Nm3 | Unknown | 2010-06-03 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.0149 | 1.794e-05 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.174 | 0.0002105 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cope 7210_COP001 | NOx: SCR, PM: FF, SO2: FGDsd | Coal-Fired Boilers | 441 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.0222 | 2.668e-05 | mg/Nm3 | Unknown | 2010-06-08 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.286 | 0.0003219 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 11.7 %CO2, 7.2 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.272 | 0.0003112 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 11.7 %CO2, 7.2 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.229 | 0.0002682 | mg/Nm3 | Unknown | 2010-05-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 13.2 %H20, 12.2 %CO2, 6.7 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.118 | 0.0001288 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %H20, 12 %CO2, 7.8 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0471 | 5.365e-05 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.4 %H20, 12 %CO2, 6.9 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0967 | 0.000118 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.4 %H20, 12 %CO2, 6.9 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0415 | 4.292e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %H20, 12.1 %CO2, 7.3 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.0732 | 8.584e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %H20, 12.1 %CO2, 7.3 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Craig 6021_C2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 456 |  | Tri-State Generation and Transmission Association | subbituminous | Rocky Mountain | Green River (CO) | Wall-fired | Opposed wall-fired boiler. | 5 |  | 0.0811 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %H20, 12 %CO2, 6.7 %O2
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 4 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 5 | NOx: SNCR, PM: ESPhc(Without Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 82 |  | Gulf Power Company | bituminous | Eastern | WV | Tangential |  | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 6 | NOx: SNCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 320 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.99 | 0.001048 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 2723749 | dscfm | 13 %H20, 124 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.8 | 0.0008466 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2664157 | dscfm | 12 %H20, %CO2, %O2, 122 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crist 641_Unit 7 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 500 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.882 | 0.0009335 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 2735272 | dscfm | 13 %H20, 123 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.152 | 0.0001609 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1681900 | dscfm | 12.9 %H20, 11.08 %CO2, 8.32 %O2, 147.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.144 | 0.0001502 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1652433 | dscfm | 12.8 %H20, 10.99 %CO2, 8.47 %O2, 147.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 610 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.155 | 0.0001609 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 1693683 | dscfm | 12.2 %H20, 10.88 %CO2, 8.58 %O2, 147.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 0.232 | 0.0003155 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1334850 | dscfm | 15.2 %H20, 14.46 %CO2, 4.93 %O2, 129.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 0.232 | 0.000308 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1344500 | dscfm | 15.1 %H20, 14.36 %CO2, 4.95 %O2, 129.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C3 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Forced ox) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 0.223 | 0.0003037 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1342567 | dscfm | 14.9 %H20, 14.38 %CO2, 4.91 %O2, 130 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 1 |  | 0.308 | 0.0003863 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1381117 | dscfm | 14.9 %H20, 13.5 %CO2, 5.99 %O2, 127.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 2 |  | 0.266 | 0.0003326 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1373950 | dscfm | 14.4 %H20, 13.4 %CO2, 6.01 %O2, 127.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Cross 130_C4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 625 |  | South Carolina Public Service Authority | bituminous | Eastern | IL, KY, WV, PA | Tangential |  | 3 |  | 0.256 | 0.0003219 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1398133 | dscfm | 14.4 %H20, 13.18 %CO2, 5.94 %O2, 127.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 3.37 | 0.004217 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 867953 | dscfm | 5.5 %H20, 65 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 3.53 | 0.00441 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 843587 | dscfm | 6.5 %H20, %CO2, %O2, 58 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Crystal River Power Plant 628_CryR_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 400 |  | Progress Energy Florida, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 3.21 | 0.004013 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 852628 | dscfm | 6.1 %H20, %CO2, %O2, 76 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 1.44 | 0.001502 | mg/Nm3 | Unknown | 2010-04-05 | Refer to sample method | U.S. EPA Method 30B | 227767 | dscfm | 6.12 %H20, 10.4 %CO2, 8.4 %O2, 316 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 1.58 | 0.001717 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 232147 | dscfm | 5.66 %H20, 10.4 %CO2, 8.4 %O2, 308 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dale Station 1385_03 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 80 |  | East KY Power Coop, Inc | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 1.75 | 0.001824 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 227224 | dscfm | 5.94 %H20, 10.2 %CO2, 8.5 %O2, 317 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.72 | 0.0008906 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 383635 | dscfm | 15.6 %H20, 12.3 %CO2, 6.3 %O2, 130.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.449 | 0.0005365 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 384645 | dscfm | 15.6 %H20, 12 %CO2, 6.8 %O2, 129.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.72 | 0.000913 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.548 | 0.000671 | mg/Nm3 | Unknown | 2010-06-29 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.449 | 0.00055 | mg/Nm3 | Unknown | 2010-06-30 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dallman 963_34 | NOx: SCR, PM: FFp, SO2: FGDw(Packed,Forced ox), SO3: ESPw | Coal-Fired Boilers | 229 |  | City Water, Light and Power, City of Springfield | bituminous | Interior(East, North) | IL | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.548 | 0.0006545 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 383568 | dscfm | 15.7 %H20, 12 %CO2, 6.8 %O2, 129.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 2 |  | 3.22 | 0.004056 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1050000 | dscfm | 18 %H20, 13 %CO2, 6.1 %O2, 135 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 3 |  | 2.97 | 0.003745 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1050000 | dscfm | 18 %H20, 13 %CO2, 6.1 %O2, 135 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Duck Creek 6016_001 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Inhibited) | Coal-Fired Boilers | 400 |  | Ameren Energy Generating Company | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Wall-fired |  | 4 |  | 3.06 | 0.003595 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1080000 | dscfm | 17 %H20, 12.4 %CO2, 6.7 %O2, 135 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1.73 | 0.002017 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.621 | 0.0007639 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_1 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 85 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 0.67 | 0.0008181 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.976 | 0.001125 | mg/Nm3 | Unknown | 2010-04-19 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1.03 | 0.001164 | mg/Nm3 | Unknown | 2010-04-19 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Dunkirk Generating Plant 2554_4 | NOx: SNCR, PM: FF, SO3: SI | Coal-Fired Boilers | 195 |  | Dunkirk Power LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.405 | 0.000481 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 4.26 | 0.004652 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 218130 | dscfm | 9.1 %H20, 11.2 %CO2, 7.9 %O2, 292 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 3.42 | 0.003734 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 218130 | dscfm | 9.1 %H20, 11.2 %CO2, 7.9 %O2, 292 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eagle Valley 991_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 3.77 | 0.003864 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 219978 | dscfm | 9.3 %H20, 10.4 %CO2, 8.7 %O2, 287 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 0.554 | 0.0005751 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1808404 | dscfm | 14.9 %H20, 11.1 %CO2, 8.56 %O2, 127.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.684 | 0.0007103 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1806975 | dscfm | 14.9 %H20, 11.06 %CO2, 8.55 %O2, 127.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | East Bend Station 6018_2 | NOx: SCR, PM: ESPh(With Conditioning), SO2: FGDw(Spray,Natural), SO3: SI | Coal-Fired Boilers | 650 |  | Duke Energy Kentucky | bituminous | Eastern, Interior(East, North) | KY, OH, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.714 | 0.0007393 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1807286 | dscfm | 14.82 %H20, 11.01 %CO2, 8.59 %O2, 127 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 3.03 | 0.002897 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 2.91 | 0.00279 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 2.42 | 0.002318 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B |  |  | 353.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 1 |  | 1.45 | 0.001363 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 344.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 2 |  | 1.89 | 0.001781 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 321.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eastlake 2837_Unit 3 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 144 |  | First Energy Generation Corp. | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Tangential |  | 3 |  | 1.37 | 0.001288 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 322.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0127 | 1.77e-05 | mg/Nm3 | Unknown | 2010-07-28 | Refer to sample method | U.S. EPA Method 30B | 163045 | dscfm | 9.13 %H20, 15.77 %CO2, 3.74 %O2, 327 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0118 | 1.609e-05 | mg/Nm3 | Unknown | 2010-07-28 | Refer to sample method | U.S. EPA Method 30B | 163045 | dscfm | 9.13 %H20, 15.77 %CO2, 3.74 %O2, 330 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Ebensburg Power Company 10603_EPC01 | NOx: Unspecified, PM: ESPc FFp | Coal-Fired Boilers | 58 |  | Babcock & Wilcox Ebensburg Power Inc. | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0131 | 1.824e-05 | mg/Nm3 | Unknown | 2010-07-29 | Refer to sample method | U.S. EPA Method 30B | 163656 | dscfm | 9.62 %H20, 15.95 %CO2, 3.71 %O2, 327 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 1.92 | 0.001989 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 961693 | dscfm | 13 %H20, 10.6 %CO2, 8.6 %O2, 214 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 1.5 | 0.001532 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 959176 | dscfm | 13 %H20, 10.4 %CO2, 8.8 %O2, 213 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Eddystone Generating Station 3161_Unit 2 | NOx: SNCR, PM: MC PS, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 339 |  | Exelon Generation Company, LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.956 | 0.0009979 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 970409 | dscfm | 13 %H20, 10.9 %CO2, 8.5 %O2, 213.3125 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0782 | 0.0001073 | mg/Nm3 | Unknown | 2010-11-08 | Refer to sample method | U.S. EPA Method 30B | 1293717 | dscfm | 13.2 %H20, 14.4 %CO2, 4.3 %O2, 126.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0655 | 7.511e-05 | mg/Nm3 | Unknown | 2010-11-09 | Refer to sample method | U.S. EPA Method 30B | 1280177 | dscfm | 13.6 %H20, 14.6 %CO2, 4.2 %O2, 127.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elm Road Generating Station 56068_ERGS-B1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 677 |  | Wisconsin Electric Power Company | bituminous | Eastern | PA, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0823 | 0.000118 | mg/Nm3 | Unknown | 2010-11-09 | Refer to sample method | U.S. EPA Method 30B | 1273325 | dscfm | 15.3 %H20, 14.6 %CO2, 4.2 %O2, 128.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR1-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR2-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 100 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR3-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 125 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Vertical-fired |  | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 1.99 | 0.002384 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 1.06 | 0.001268 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Elrama Power Plant 3098_ELR4-2 | NOx: SNCR, PM: MC ESPc(Without Conditioning), SO2: FGDw(Venturi,Inhibited) | Coal-Fired Boilers | 185 |  | Orion Power Midwest LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 0.292 | 0.0003503 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.17 | 0.002792 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.32 | 0.003044 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Erickson Station 1832_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 165 |  | City of Lansing, Board of Water & Light | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.75 | 0.003444 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 5.56 | 0.00764 | mg/Nm3 | Unknown | 2010-08-03 | Refer to sample method | U.S. EPA Method 30B | 94232 | dscfm | 9.5 %H20, 14.7 %CO2, 4.9 %O2, 334 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 5.46 | 0.007178 | mg/Nm3 | Unknown | 2010-08-04 | Refer to sample method | U.S. EPA Method 30B | 98388 | dscfm | 9.6 %H20, 14.1 %CO2, 5.6 %O2, 341 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Fair Station 1218_U2 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 44 |  | Central Iowa Power Cooperative | bituminous | Unknown | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 5.39 | 0.007007 | mg/Nm3 | Unknown | 2010-08-05 | Refer to sample method | U.S. EPA Method 30B | 97307 | dscfm | 9.3 %H20, 13.5 %CO2, 5.7 %O2, 342 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.428 | 0.0005479 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 1252777 | dscfm | 11.61 %H20, 13.85 %CO2, 5.67 %O2, 124.04166667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.858 | 0.001111 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1248035 | dscfm | 12.04 %H20, 13.94 %CO2, 5.5 %O2, 124.20833333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_3-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 282 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.928 | 0.001208 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1262491 | dscfm | 12.35 %H20, 13.91 %CO2, 5.41 %O2, 125.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.428 | 0.0005479 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 1252777 | dscfm | 11.61 %H20, 13.85 %CO2, 5.67 %O2, 124.04166667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.858 | 0.001111 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1248035 | dscfm | 12.04 %H20, 13.94 %CO2, 5.5 %O2, 124.20833333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | G G Allen 2718_4-2009-FGDIN | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 297 |  | Duke Energy Corporation | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.928 | 0.001208 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B | 1262491 | dscfm | 12.7 %H20, 13.91 %CO2, 5.41 %O2, 125.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 6.5 | 0.007618 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 541060 | dscfm | 11.7 %H20, 12.72 %CO2, 6.97 %O2, 331.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 6.1 | 0.007189 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 550024 | dscfm | 10.4 %H20, 12.7 %CO2, 6.98 %O2, 336.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gallatin 3403_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 300 |  | Tennessee Valley Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 6 |  | 6 | 0.006974 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 545582 | dscfm | 10.5 %H20, 12.72 %CO2, 6.98 %O2, 337.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 4.93 | 0.00629 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.7 %O2, 295.79 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 6.16 | 0.007865 | mg/Nm3 | Unknown | 2010-03-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.7 %O2, 290.79 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 715 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 6.21 | 0.007964 | mg/Nm3 | Unknown | 2010-03-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 5.8 %O2, 290.58 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 5.89 | 0.006978 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.8 %O2, 289 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 6.46 | 0.007594 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.9 %O2, 282.04 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gerald Gentleman 6077_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 750 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.84 | 0.006916 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %H20, 6.7 %O2, 269.08 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1 | 0.001241 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1529688 | dscfm | 16.3 %H20, 13.19 %CO2, 6.18 %O2, 134.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.835 | 0.001033 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1534516 | dscfm | 16.1 %H20, 13.23 %CO2, 6.18 %O2, 134.08333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_1-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.812 | 0.001005 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 1523991 | dscfm | 16.3 %H20, 13.2 %CO2, 6.17 %O2, 134.33333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.899 | 0.001088 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B | 1621345 | dscfm | 16.4 %H20, 12.98 %CO2, 6.51 %O2, 134.25 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.85 | 0.001038 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1593391 | dscfm | 16.7 %H20, 13.16 %CO2, 6.38 %O2, 134.58333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Gibson 6113_2-2007-FGDIN | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 661 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IL, IN | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.79 | 0.0009689 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 1591911 | dscfm | 16.6 %H20, 13.23 %CO2, 6.32 %O2, 135.25 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.643 | 0.0006921 | mg/Nm3 | Unknown | 2010-06-08 | Refer to sample method | U.S. EPA Method 30B | 298566 | dscfm | 8.2 %H20, 11.1 %CO2, 8.3 %O2, 369.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.684 | 0.0007296 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 304343 | dscfm | 8.2 %H20, 10.6 %CO2, 8.9 %O2, 359.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Grant Town Power Plant 10151_GEN1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 95 |  | American Bituminous Power Partners LP | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.808 | 0.0008691 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 299138 | dscfm | 8.2 %H20, 10.7 %CO2, 8.7 %O2, 363.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.37 | 0.0003863 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 672028 | dscfm | 15.68 %H20, 10.4 %CO2, 8.4 %O2, 130 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.459 | 0.0004828 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 672028 | dscfm | 15.68 %H20, 10.4 %CO2, 8.4 %O2, 130 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 01 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray), SO3: ESPw | Coal-Fired Boilers | 344 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.737 | 0.0007618 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 693034 | dscfm | 12.25 %H20, 10.3 %CO2, 8.6 %O2, 130 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 0.0743 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 577269 | dscfm | 12.74 %H20, 14.6 %CO2, 4.9 %O2, 170 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 0.0709 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 585395 | dscfm | 12.44 %H20, 14.6 %CO2, 5 %O2, 158 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 03 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 0.0708 | 9.657e-05 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 577269 | dscfm | 12.74 %H20, 14.6 %CO2, 4.9 %O2, 170 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 1 |  | 0.191 | 0.0002575 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 527403 | dscfm | 11.03 %H20, 14.3 %CO2, 5.1 %O2, 176 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 2 |  | 0.191 | 0.0002039 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 524523 | dscfm | 9.7 %H20, 10.4 %CO2, 8.4 %O2, 200 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | H L Spurlock Station 6041_Unit 04 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 300 |  | East KY Power | bituminous | Interior(East, North), Eastern | IL, KY, OH, WV | Fluidized bed |  | 3 |  | 0.131 | 0.0001395 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 524523 | dscfm | 9.7 %H20, 10.2 %CO2, 8.5 %O2, 203 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 1 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 2 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 3 | NOx: Unspecified, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 115 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.544 | 0.0005365 | mg/Nm3 | Unknown | 2010-02-02 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.601 | 0.0006009 | mg/Nm3 | Unknown | 2010-02-03 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hammond 708_Unit 4 | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 520 |  | Georgia Power | bituminous | Eastern | TN, VA, KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.671 | 0.0006974 | mg/Nm3 | Unknown | 2010-02-11 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 3.75 | 0.004388 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 3.21 | 0.003588 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_60s | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 114 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 4.44 | 0.005099 | mg/Nm3 | Unknown | 2010-03-07 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 1 |  | 1.07 | 0.001113 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 2 |  | 0.999 | 0.001084 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Harding Street 990_70ss | NOx: SCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray), SO3: SI | Coal-Fired Boilers | 471 |  | Indianapolis Power & Light Company | bituminous | Interior(East, North) | IL, IN | Tangential |  | 3 |  | 0.892 | 0.0009421 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 3.23 | 0.004464 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1158508 | dscfm | 13.54 %H20, 14.72 %CO2, 4.42 %O2, 125.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 3.07 | 0.004131 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1159417 | dscfm | 14.62 %H20, 14.29 %CO2, 4.82 %O2, 125.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hatfield's Ferry Power Station 3179_001 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 590 |  | Allegheny Energy Supply Company LLC | bituminous | Eastern | PA, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.17 | 0.004335 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 181644 | dscfm | 14.5 %H20, 14.33 %CO2, 4.64 %O2, 125.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.153 | 0.0001953 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B | 2807920 | dscfm | 12.1 %H20, 9.9 %CO2, 6.8 %O2, 313 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.172 | 0.0002146 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 3018141 | dscfm | 12.5 %H20, 9.9 %CO2, 6.9 %O2, 312.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Havana 891_Boiler 9 | NOx: SCR, PM: ESPh FF, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 481 |  | Dynegy Midwest Generation Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.154 | 0.0001931 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3722116 | dscfm | 12.3 %H20, 9.9 %CO2, 6.8 %O2, 307.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 4.97 | 0.006352 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1291029 | dscfm | 14.75 %H20, 13.8 %CO2, 5.7 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 5.02 | 0.005998 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1257291 | dscfm | 14.69 %H20, 13.8 %CO2, 5.7 %O2, 186 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hawthorn 2079_5A | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 594 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains, Rocky Mountain | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 4 |  | 5.91 | 0.006599 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 1262082 | dscfm | 14.79 %H20, 13.8 %CO2, 5.7 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.304 | 0.0003809 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 490000 | dscfm | 14.3 %H20, 165 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.445 | 0.000558 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 504000 | dscfm | 14.5 %H20, 166 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 202 |  | Public Service Company of Colorado | bituminous | Northern Great Plains, Rocky Mountain | Powder River Basin, Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.252 | 0.0003155 | mg/Nm3 | Unknown | 2010-02-19 | Refer to sample method | U.S. EPA Method 30B | 517000 | dscfm | 14 %H20, 165 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 1 |  | 0.549 | 0.0006889 | mg/Nm3 | Unknown | 2010-02-23 | Refer to sample method | U.S. EPA Method 30B | 591000 | dscfm | 12.9 %H20, 167 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 2 |  | 0.588 | 0.0007372 | mg/Nm3 | Unknown | 2010-02-24 | Refer to sample method | U.S. EPA Method 30B | 594000 | dscfm | 13.3 %H20, 166 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hayden 525_Unit 2 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 285 |  | Public Service Company of Colorado | bituminous | Rocky Mountain | Green River (CO) | Tangential |  | 3 |  | 0.518 | 0.0006492 | mg/Nm3 | Unknown | 2010-02-25 | Refer to sample method | U.S. EPA Method 30B | 587000 | dscfm | 13.3 %H20, 166 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 0.955 | 0.001225 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 386007 | dscfm | 7.37 %H20, 13.44 %CO2, 5.64 %O2, 268.42 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 0.396 | 0.0005075 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 386007 | dscfm | 7.37 %H20, 13.44 %CO2, 5.64 %O2, 274.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.746 | 0.0009442 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 390701 | dscfm | 7.11 %H20, 13.24 %CO2, 5.85 %O2, 268.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 0.902 | 0.001142 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 390701 | dscfm | 7.11 %H20, 13.24 %CO2, 5.85 %O2, 263.17 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | HB Robinson / Darlington Electric Power Plant 3251_Rob_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 187 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 0.301 | 0.0003831 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 383265 | dscfm | 7.37 %H20, 13.32 %CO2, 5.74 %O2, 262.92 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.091 | 0.000117 | mg/Nm3 | Unknown | 2010-08-24 | Refer to sample method | U.S. EPA Method 30B | 800402 | dscfm | 12 %H20, 12 %CO2, 6 %O2, 361.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.184 | 0.0002361 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 762163 | dscfm | 11.1 %H20, 12.1 %CO2, 6.1 %O2, 358.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 75 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.21 | 0.0002661 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 767078 | dscfm | 11.4 %H20, 11.9 %CO2, 6.3 %O2, 360.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.091 | 0.000117 | mg/Nm3 | Unknown | 2010-08-24 | Refer to sample method | U.S. EPA Method 30B | 800402 | dscfm | 12 %H20, 12 %CO2, 6 %O2, 361.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.184 | 0.0002361 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 762163 | dscfm | 11.1 %H20, 12.1 %CO2, 6.1 %O2, 358.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hennepin Power Station 892_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 234 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.21 | 0.0002661 | mg/Nm3 | Unknown | 2010-08-25 | Refer to sample method | U.S. EPA Method 30B | 767078 | dscfm | 11.4 %H20, 11.9 %CO2, 6.3 %O2, 360.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.73 | 0.006893 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.18 | 0.006538 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hoot Lake 1943_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 61 |  | Otter Tail Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 6.82 | 0.008548 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 |  | 0.0506 | 6.545e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 177882 | dscfm | 13.43 %H20, 13.55 %CO2, 5.55 %O2, 210.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 |  | 0.0378 | 4.936e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 177690 | dscfm | 14.06 %H20, 13.66 %CO2, 5.4 %O2, 210.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Hopewell 10771_1 & 2 | NOx: SNCR, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 |  | 0.0494 | 6.331e-05 | mg/Nm3 | Unknown | 2010-04-24 | Refer to sample method | U.S. EPA Method 30B | 175659 | dscfm | 14.03 %H20, 13.43 %CO2, 5.63 %O2, 213.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0204 | 2.5e-05 | mg/Nm3 | Unknown | 2010-06-03 | Refer to sample method | U.S. EPA Method 30B | 692930 | dscfm | 9 %CO2, %O2, 192.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.00729 | 8.906e-06 | mg/Nm3 | Unknown | 2010-06-04 | Refer to sample method | U.S. EPA Method 30B | 711516 | dscfm | 9.4 %CO2, %O2, 192.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | INDIANTOWN COGENERATION L.P. 50976_001 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 361 |  | INDIANTOWN COGENERATION L.P. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.00263 | 3.219e-06 | mg/Nm3 | Unknown | 2010-06-04 | Refer to sample method | U.S. EPA Method 30B | 711516 | dscfm | 9.4 %CO2, %O2, 192.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 3.12 | 0.003809 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 2.92 | 0.003562 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J K Spruce 7097_1 | NOx: Unspecified, PM: FFr, SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 580 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.48 | 0.004249 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.79 | 0.007889 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 7.71 | 0.01064 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 5.83 | 0.008091 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.79 | 0.007889 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 7.71 | 0.01064 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | J T Deely 6181_2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 450 |  | City Public Service San Antonio | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 5.83 | 0.008091 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 4.27 | 0.005869 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 3.36 | 0.004625 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James H. Miller Jr. 6002_Unit 4 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 723 |  | Alabama Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 3.38 | 0.004646 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 1 | < | 0.169 | 0.0002245 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 2 | < | 0.174 | 0.0002282 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Cogeneration Co 10377_UNIT2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 19 |  | James River Cogeneration Co | bituminous | Eastern | KY, VA | Stoker | Underfeed stoker boiler. | 3 | < | 0.166 | 0.0002205 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.77 | 0.003221 | mg/Nm3 | Unknown | 2010-06-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.79 | 0.003291 | mg/Nm3 | Unknown | 2010-06-23 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_4_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 60 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 4 |  | 2.62 | 0.003139 | mg/Nm3 | Unknown | 2010-06-24 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.12 | 0.002484 | mg/Nm3 | Unknown | 2010-04-26 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.67 | 0.003012 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | James River Power Station 2161_Unit_5_JRPS | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 105 |  | City Utilities of Springfield | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 1.79 | 0.002042 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1.3 | 0.001609 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 686055 | dscfm | 12 %H20, 13.4 %CO2, 6.1 %O2, 300.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 0.935 | 0.001223 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 698344 | dscfm | 11.8 %H20, 13.7 %CO2, 5.8 %O2, 296 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joliet 9 874_JOL5 CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 326 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1.01 | 0.001277 | mg/Nm3 | Unknown | 2010-06-17 | Refer to sample method | U.S. EPA Method 30B | 705100 | dscfm | 11.9 %H20, 13.4 %CO2, 6 %O2, 300.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.44 | 0.001813 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | U.S. EPA Method 30B | 821000 | dscfm | 13.7 %H20, 13.2 %CO2, 5.8 %O2, 337 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 2.46 | 0.003122 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B | 836000 | dscfm | 13.3 %H20, 13.2 %CO2, 5.7 %O2, 339 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Joppa Steam 887_1 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 183 |  | Electric Energy, Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2.19 | 0.002801 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 832000 | dscfm | 13.3 %H20, 13.3 %CO2, 5.6 %O2, 339 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 6.88 | 0.009142 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 1590359 | dscfm | 12.57 %H20, 14.11 %CO2, 5.3 %O2, 296.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 4.93 | 0.006299 | mg/Nm3 | Unknown | 2010-05-21 | Refer to sample method | U.S. EPA Method 30B | 1562204 | dscfm | 13.09 %H20, 14.26 %CO2, 5.24 %O2, 297 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 6.37 | 0.008208 | mg/Nm3 | Unknown | 2010-05-22 | Refer to sample method | U.S. EPA Method 30B | 1509097 | dscfm | 13.13 %H20, 13.77 %CO2, 4.99 %O2, 294 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | La Cygne 1241_2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 685 |  | Kansas City Power & Light Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 4 |  | 5.66 | 0.00764 | mg/Nm3 | Unknown | 2010-05-22 | Refer to sample method | U.S. EPA Method 30B | 1509097 | dscfm | 13.13 %H20, 13.77 %CO2, 4.99 %O2, 294 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.77 | 0.001985 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 269318 | dscfm | 10.6 %H20, 11.5 %CO2, 7.5 %O2, 342 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 2.28 | 0.002554 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 259822 | dscfm | 10.7 %H20, 11.8 %CO2, 7.7 %O2, 336 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lake Road 2098_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 99 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.64 | 0.001835 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 266114 | dscfm | 10.7 %H20, 12 %CO2, 7.6 %O2, 328 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.12 | 0.005494 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.14 | 0.006899 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Lawrence Energy Center 1250_3 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 58 |  | Westar Energy Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.72 | 0.004979 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 140164 | dscfm | 11.7 %H20, 14.4 %CO2, 5.3 %O2, 325 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 7.38 | 0.008687 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 6.49 | 0.007685 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Louisa 6664_101 | NOx: Unspecified, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 805 |  | MidAmerican Energy Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 6.84 | 0.008111 | mg/Nm3 | Unknown | 2010-04-27 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0583 | 7.296e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0261 | 3.273e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 5 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 55 |  | Colorado Springs, City of | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0281 | 3.519e-05 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0316 | 3.745e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0261 | 3.09e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Martin Drake 492_Unit 7 - Coal | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 141 |  | Colorado Springs, City of | subbit/bit | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0357 | 4.238e-05 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 1 |  | 0.109 | 0.0001309 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 2 |  | 0.0969 | 0.0001163 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 135 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 3 | < | 0.0598 | 7.215e-05 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 1 |  | 0.0432 | 5.419e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 2 |  | 0.0525 | 6.631e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | McMeekin 3287_MCM002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 132 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN, WV | Tangential |  | 3 | < | 0.0402 | 5.053e-05 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0632 | 8.563e-05 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 357057 | dscfm | 11.18 %H20, 14.69 %CO2, 4.79 %O2, 181 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0571 | 7.554e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 368805 | dscfm | 11.31 %H20, 14.36 %CO2, 5.15 %O2, 176 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Mecklenburg Power Station 52007_Unit 1 & 2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 76 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0677 | 9.024e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 358184 | dscfm | 11.66 %H20, 14.34 %CO2, 5.11 %O2, 173 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 5 |  | 1.91 | 0.002507 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 7 |  | 1.66 | 0.002231 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Meredosia 864_005 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 204 |  | Ameren Energy Generating Company | bituminous | Northern Great Plains | Powder River Basin | Tangential |  | 6 |  | 1.82 | 0.002438 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B | 532596 | dscfm | 11.7 %H20, 13.9 %CO2, 5.5 %O2, 342.806 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 1 |  | 7.7 | 0.01063 | mg/Nm3 | Unknown | 2010-03-29 | Refer to sample method | U.S. EPA Method 30B | 625992 | dscfm | 7.7 %H20, 15.54 %CO2, 3.76 %O2, 335.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 2 |  | 9.03 | 0.01245 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B | 628494 | dscfm | 8.3 %H20, 15.43 %CO2, 3.83 %O2, 335.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Merrimack Station 2364_mk2 | NOx: SCR, PM: ESPc(Without Conditioning), SO3: SI, Hg: ACSI | Coal-Fired Boilers | 337 |  | Public Service Company of New Hampshire | bituminous | Eastern | PA | Cyclone |  | 3 |  | 7.8 | 0.01076 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B | 629793 | dscfm | 8.3 %H20, 15.31 %CO2, 3.88 %O2, 334.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 5.93 | 0.006685 | mg/Nm3 | Unknown | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 1196818 | dscfm | 7.08 %H20, %CO2, %O2, 74 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 6.69 | 0.007532 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 1202596 | dscfm | 6.92 %H20, 66 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Michigan City 997_12 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 495 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 7.86 | 0.008852 | mg/Nm3 | Unknown | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 1197709 | dscfm | 6.52 %H20, %CO2, %O2, 76 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 6.17 | 0.007718 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1278916 | dscfm | 12.45 %H20, 13.3 %CO2, 6.3 %O2, 376 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 4 |  | 6.33 | 0.007973 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1290170 | dscfm | 12.65 %H20, 13.5 %CO2, 6.2 %O2, 378 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Monticello 6147_2 | NOx: SNCR, PM: ESPc(With Conditioning) FF, Hg: ACSI | Coal-Fired Boilers | 583 |  | Luminant Generation Company LLC | lignite | Gulf | TX | Tangential |  | 5 |  | 7.58 | 0.009551 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1283352 | dscfm | 10.01 %H20, 13.5 %CO2, 6.2 %O2, 392 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 1 |  | 0.773 | 0.001091 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 163426 | dscfm | 6.49 %H20, 14.72 %CO2, 4.28 %O2, 412 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 2 |  | 0.879 | 0.001239 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 163351 | dscfm | 7.17 %H20, 14.79 %CO2, 4.1 %O2, 415 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Morgantown Energy Facility 10743_Unit 1&2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 58 |  | Morgantown Energy Associates | waste unknown | Eastern | WV | Fluidized bed |  | 3 |  | 0.922 | 0.001313 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B | 160792 | dscfm | 7.82 %H20, 14.77 %CO2, 4.1 %O2, 417 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 | UNK | 3.48 | 0.004755 | mg/Nm3 | Poor | 2010-07-13 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 | UNK | 3.72 | 0.005115 | mg/Nm3 | Poor | 2010-07-13 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Muscatine #1 1167_8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 75 |  | Board of Water, Electric & Communications Trustees | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 | UNK | 3.59 | 0.004948 | mg/Nm3 | Poor | 2010-07-14 | Not Specified | EPA method 29 |  |  |  | No lab data available. Data flag not reported.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.24 | 0.002674 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1366625 | dscfm | 16.4 %H20, 14.9 %CO2, 5.2 %O2, 187 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2 | 0.002406 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1362778 | dscfm | 16.6 %H20, 14.9 %CO2, 5.2 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 2.24 | 0.002674 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1366625 | dscfm | 16.4 %H20, 14.9 %CO2, 5.2 %O2, 187 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2 | 0.002406 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 1362778 | dscfm | 16.6 %H20, 14.9 %CO2, 5.2 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.42 | 0.002965 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1357797 | dscfm | 16.4 %H20, 15.1 %CO2, 5.1 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nebraska City 6096_NC2 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 663 |  | Omaha Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 2.42 | 0.002965 | mg/Nm3 | Unknown | 2010-07-16 | Refer to sample method | U.S. EPA Method 30B | 1357797 | dscfm | 16.4 %H20, 15.1 %CO2, 5.1 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.0996 | 0.0001374 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 1390000 | dscfm | 13.6 %H20, 14 %CO2, 5.2 %O2, 354 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.106 | 0.0001458 | mg/Nm3 | Unknown | 2010-06-17 | Refer to sample method | U.S. EPA Method 30B | 1310000 | dscfm | 13.6 %H20, 13.9 %CO2, 4.8 %O2, 341 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Newton 6017_002 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 620 |  | Ameren Energy Generating Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 4 |  | 0.106 | 0.0001466 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 1310000 | dscfm | 14 %H20, 12.9 %CO2, 5.2 %O2, 347 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.00897 | 1.17e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 290557 | dscfm | 8.15 %H20, 14.5 %CO2, 5.43 %O2, 322.83 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0184 | 2.393e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 271693 | dscfm | 8.32 %H20, 15.3 %CO2, 5.4 %O2, 324.83 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Northampton Generating Company, L.P. 50888_GEN1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 121 |  | Northampton Generating Company, L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0179 | 2.328e-05 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 281639 | dscfm | 7.03 %H20, 15.7 %CO2, 5.36 %O2, 307.43 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 1 |  | 0.00981 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B |  |  | 6.4 %H20, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 2 |  | 0.00965 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B |  |  | 6.5 %H20, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Nucla 527_001 | NOx: SNCR, PM: FF | Coal-Fired Boilers | 110 |  | Tri-State Generation and Transmission Association | bituminous | Rocky Mountain | Green River (CO) | Fluidized bed |  | 3 |  | 0.0101 | 1.073e-05 | mg/Nm3 | Unknown | 2010-05-15 | Refer to sample method | U.S. EPA Method 30B |  |  | 5.8 %H20, 11.4 %CO2, 7.8 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 1 |  | 1.27 | 0.001556 | mg/Nm3 | Unknown | 2010-05-18 | Refer to sample method | U.S. EPA Method 30B | 1828760 | dscfm | 21.78 %H20, 13.41 %CO2, 6.21 %O2, 144 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 2 |  | 0.924 | 0.001266 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1793768 | dscfm | 21.23 %H20, 15.16 %CO2, 4.47 %O2, 143 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Oak Grove 6180_OG1 | NOx: SCR, PM: FFp, SO2: FGDw(Spray), Hg: ACSI | Coal-Fired Boilers | 817 |  | Oak Grove Management Company LLC | lignite | Gulf | TX | Tangential |  | 3 |  | 1.14 | 0.001556 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1835111 | dscfm | 21.23 %H20, 15.08 %CO2, 4.51 %O2, 143 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0434 | 4.989e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.96 %CO2, 6.37 %O2, 337.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0473 | 5.365e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.94 %CO2, 6.4 %O2, 344.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG1 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0333 | 3.97e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.42 %H20, 14.01 %CO2, 6.32 %O2, 339.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.0434 | 4.989e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.96 %CO2, 6.37 %O2, 337.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.0473 | 5.365e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.04 %H20, 13.94 %CO2, 6.4 %O2, 344.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PANTHER CREEK ENERGY FACILITY 50776_BG2 | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 47 |  | PANTHER CREEK PARTNERS | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.0333 | 3.97e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B | 266404 | dscfm | 7.42 %H20, 14.01 %CO2, 6.32 %O2, 339.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.12 | 0.0001609 | mg/Nm3 | Unknown | 2010-06-02 | Refer to sample method | U.S. EPA Method 30B | 93746 | dscfm | 8.37 %H20, 15.47 %CO2, 4.64 %O2, 341.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.118 | 0.0001609 | mg/Nm3 | Unknown | 2010-06-03 | Refer to sample method | U.S. EPA Method 30B | 91738 | dscfm | 9.05 %H20, 15.57 %CO2, 4.51 %O2, 342.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Piney Creek Project 54144_BRBRI | NOx: SNCR, PM: FFp | Coal-Fired Boilers | 36 |  | Colmac Clarion, Inc. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.144 | 0.0001931 | mg/Nm3 | Unknown | 2010-06-01 | Refer to sample method | U.S. EPA Method 30B | 94701 | dscfm | 9 %H20, 15.42 %CO2, 4.56 %O2, 346.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 1 |  | 1.21 | 0.001581 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 |  | 1.12 | 0.001456 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Tray) | Coal-Fired Boilers | 330 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 |  | 1.2 | 0.001567 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 1 |  | 1.21 | 0.001581 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 2 |  | 1.12 | 0.001456 | mg/Nm3 | Unknown | 2010-04-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Brunner Island 3140_U2 | NOx: Unspecified, PM: ESPc(Without Conditioning), SO2: FGDw(Tray) | Coal-Fired Boilers | 393 |  | PPL Brunner Island LLC | bituminous | Eastern | OH, PA, WV | Tangential |  | 3 |  | 1.2 | 0.001567 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 1 |  | 0.373 | 0.0004335 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1627239 | dscfm | 120.52 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 0.222 | 0.0002575 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1620043 | dscfm | 120.96 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 797 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.255 | 0.0002983 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1640091 | dscfm | 120.33 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 2 |  | 0.421 | 0.0005032 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1761667 | dscfm | 11.4 %H20, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 3 |  | 0.515 | 0.0006148 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1761667 | dscfm | 11.4 %H20, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PPL Montour 3149_U2 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Tray), SO3: SI | Coal-Fired Boilers | 792 |  | PPL Montour LLC | bituminous | Eastern | WV, PA | Tangential |  | 4 |  | 0.395 | 0.0004678 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 1759587 | dscfm | 11.58 %H20, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 1 |  | 0.325 | 0.0003723 | mg/Nm3 | Unknown | 2010-02-17 | Refer to sample method | U.S. EPA Method 30B | 654237 | dscfm | 6.97 %H20, 11.86 %CO2, 7.28 %O2, 307.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 3 |  | 0.326 | 0.0003745 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 650476 | dscfm | 7.18 %H20, 11.8 %CO2, 7.24 %O2, 311 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU1E1PT1OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 4 |  | 0.304 | 0.0003541 | mg/Nm3 | Unknown | 2010-02-18 | Refer to sample method | U.S. EPA Method 30B | 704425 | dscfm | 7.13 %H20, 11.98 %CO2, 7.07 %O2, 314.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 2 |  | 0.47 | 0.0005386 | mg/Nm3 | Unknown | 2010-02-09 | Refer to sample method | U.S. EPA Method 30B | 702720 | dscfm | 6.4 %H20, 11.86 %CO2, 7.28 %O2, 315.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 4 |  | 0.463 | 0.0005236 | mg/Nm3 | Unknown | 2010-02-12 | Refer to sample method | U.S. EPA Method 30B | 578620 | dscfm | 6.8 %H20, 11.8 %CO2, 7.24 %O2, 305.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | PSEG Mercer Generating Station 2408_MERU2E2PT2OS1-Coal | NOx: SCR, PM: ESPc(With Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 343 |  | PSEG Fossil, LLC | bituminous | Eastern | VA | Wall-fired |  | 5 |  | 0.508 | 0.0005891 | mg/Nm3 | Unknown | 2010-02-13 | Refer to sample method | U.S. EPA Method 30B | 699821 | dscfm | 5.94 %H20, 11.98 %CO2, 7.07 %O2, 313.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 1 |  | 8.48 | 0.01137 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 2 |  | 5.66 | 0.007629 | mg/Nm3 | Unknown | 2010-04-07 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 3 |  | 5.71 | 0.007361 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Pulliam 4072_8 | NOx: Unspecified, PM: ESPc(With Conditioning), Hg: ACSI | Coal-Fired Boilers | 138 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Rear wall-fired boiler. | 4 |  | 5.4 | 0.006964 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.82 | 0.00606 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 268362 | dscfm | 10.7 %H20, 11.8 %CO2, 8.2 %O2, 311 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 4.31 | 0.004625 | mg/Nm3 | Unknown | 2010-06-18 | Refer to sample method | U.S. EPA Method 30B | 258116 | dscfm | 10.5 %H20, 11.3 %CO2, 8.8 %O2, 304 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Quindaro 1295_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 120 |  | The Kansas City Board of Public Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 2.69 | 0.003233 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 266685 | dscfm | 11.1 %H20, 12.4 %CO2, 7.7 %O2, 313 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 1.33 | 0.001497 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1059520 | dscfm | 12.8 %CO2, 5.4 %O2, 285 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1.06 | 0.001281 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 1066226 | dscfm | 12.8 %CO2, 5.4 %O2, 294 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | R.M. Schahfer 6085_R.M.0014 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 468 |  | Northern Indiana Public Service Company | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 1.29 | 0.001575 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B | 1058820 | dscfm | 12.7 %CO2, 5 %O2, 287 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.11 | 0.005075 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 550371 | dscfm | 12.9 %H20, 13.5 %CO2, 6.4 %O2, 200 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 5.88 | 0.007318 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 703316 | dscfm | 13.7 %H20, 13.2 %CO2, 6.13 %O2, 200 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Rawhide 6761_Rawhide101 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 305 |  | Platte River Power Authority | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 6.91 | 0.008573 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 719304 | dscfm | 12.8 %H20, 13.5 %CO2, 6.33 %O2, 204 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 6.01 | 0.008021 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 14.6 | 0.01975 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_001 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 11.7 | 0.01558 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 1 |  | 6.01 | 0.008021 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 2 |  | 14.6 | 0.01975 | mg/Nm3 | Unknown | 2010-05-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Red Hills Generating Facility 55076_002 | NOx: Unspecified, PM: FF | Coal-Fired Boilers | 250 |  | SE Choctaw LLC | lignite | Gulf | MS | Fluidized bed |  | 3 |  | 11.7 | 0.01558 | mg/Nm3 | Unknown | 2010-05-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.00952 | 9.657e-06 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 283691 | dscfm | 11.789 %H20, 10.843 %CO2, 8.819 %O2, 135.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.017 | 1.824e-05 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 279109 | dscfm | 11.8 %H20, 10.939 %CO2, 8.625 %O2, 136.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Reid Gardner 2324_1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Venturi,Natural) | Coal-Fired Boilers | 111 |  | Nevada Power Company | bituminous | Rocky Mountain | Green River (CO), Uinta (UT) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0337 | 3.541e-05 | mg/Nm3 | Unknown | 2010-05-08 | Refer to sample method | U.S. EPA Method 30B | 282405 | dscfm | 11.5 %H20, 10.7 %CO2, 8.9 %O2, 137.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 1 |  | 10.1 | 0.01016 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 245984 | dscfm | 7.18 %H20, 9.6 %CO2, 9.6 %O2, 317 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 2 |  | 9.16 | 0.00874 | mg/Nm3 | Unknown | 2010-06-15 | Refer to sample method | U.S. EPA Method 30B | 247799 | dscfm | 7.55 %H20, 9.9 %CO2, 9.4 %O2, 316 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Richard Gorsuch 7286_UNIT3 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 53 |  | American Municipal Power, Inc. | bituminous | Eastern | KY, OH, WV | Wall-fired |  | 3 |  | 10.9 | 0.01073 | mg/Nm3 | Unknown | 2010-06-16 | Refer to sample method | U.S. EPA Method 30B | 249097 | dscfm | 7.69 %H20, 10.1 %CO2, 9.2 %O2, 316 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 1 |  | 5.77 | 0.006866 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 30B | 131488 | dscfm | 7.3 %H20, 12.65 %CO2, 6.76 %O2, 327.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 2 |  | 7.99 | 0.009517 | mg/Nm3 | Unknown | 2010-04-12 | Refer to sample method | U.S. EPA Method 30B | 132118 | dscfm | 7.2 %H20, 12.8 %CO2, 6.73 %O2, 323.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Riverbend 2732_7 | NOx: SNCR, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 100 |  | Duke Energy Carolinas, LLC | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 8.52 | 0.01002 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 128052 | dscfm | 6.91 %O2, 318 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.00643 | 7.511e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.2 %CO2, 7 %O2, 171 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.00551 | 6.438e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.1 %CO2, 7.5 %O2, 171 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley I 54035_Boiler 1 | NOx: Unspecified, PM: FFr, SO2: FGDsd | Coal-Fired Boilers | 182 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.00441 | 5.15e-06 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 383153 | dscfm | 11.2 %H20, 11.1 %CO2, 7.6 %O2, 171 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0167 | 1.878e-05 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.2 %CO2, 7.4 %O2
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0124 | 1.395e-05 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11 %CO2, 7.5 %O2, Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roanoke Valley II 54755_Boiler 2 | NOx: SNCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 50 |  | Westmoreland Partners, LLC | bituminous | Eastern | KY | Wall-fired | Front wall-fired boiler. | 3 |  | 0.00571 | 6.438e-06 | mg/Nm3 | Unknown | 2010-06-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.2 %CO2, 7.4 %O2
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.111 | 0.0001449 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 844209 | dscfm | 12.7 %H20, 13.796 %CO2, 5.434 %O2, 120.58333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.109 | 0.0001416 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 844209 | dscfm | 12.7 %H20, 13.796 %CO2, 5.434 %O2, 120.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.139 | 0.0001792 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 837533 | dscfm | 21.7 %H20, 13.693 %CO2, 5.525 %O2, 120.25 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 4 |  | 0.115 | 0.0001491 | mg/Nm3 | Unknown | 2010-03-18 | Refer to sample method | U.S. EPA Method 30B | 837533 | dscfm | 12.6 %H20, 13.693 %CO2, 5.525 %O2, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_1b | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 385 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 5 |  | 0.173 | 0.000221 | mg/Nm3 | Unknown | 2010-03-19 | Refer to sample method | U.S. EPA Method 30B | 856761 | dscfm | 12.9 %H20, 13.585 %CO2, 5.672 %O2, 120.83333333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 3 |  | 0.15 | 0.0001985 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1434478 | dscfm | 13 %H20, 13.979 %CO2, 5.145 %O2, 121.91666667 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 4 |  | 0.185 | 0.0002457 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 1434478 | dscfm | 13 %H20, 13.979 %CO2, 5.145 %O2, 121.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 5 |  | 0.124 | 0.0001642 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1482128 | dscfm | 12.9 %H20, 14.067 %CO2, 5.122 %O2, 120.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 6 |  | 0.142 | 0.0001878 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1482128 | dscfm | 13 %H20, 14.067 %CO2, 5.122 %O2, 121.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Roxboro Steam Electric Plant 2712_Rox_Cfg_2c | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray, Tray) | Coal-Fired Boilers | 703 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Tangential |  | 7 |  | 0.154 | 0.0002039 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 1419396 | dscfm | 12.9 %H20, 13.984 %CO2, 5.142 %O2, 121 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 6.64 | 0.009153 | mg/Nm3 | Unknown | 2010-07-13 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 6.6 | 0.008987 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | RS Nelson 1393_001 | NOx: Unspecified, PM: ESP | Coal-Fired Boilers | 580 |  | Entergy Gulf States Louisiana LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 8.57 | 0.01204 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 1 |  | 0.448 | 0.000503 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 152023 | dscfm | 8.42 %H20, 11.746 %CO2, 7.899 %O2, 296.6 Deg F | Results may be biased low due to matrix interference.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 2 |  | 0.514 | 0.0005704 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 154852 | dscfm | 8.87 %H20, 11.61 %CO2, 8.052 %O2, 300.5 Deg F | Results may be biased low due to matrix interference.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Salem Harbor 1626_Unit 1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 81 |  | Dominion Salem Harbor LLC | bituminous | Eastern | Unknown | Wall-fired | Front wall-fired boiler. | 3 |  | 0.232 | 0.0002844 | mg/Nm3 | Poor | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 142931 | dscfm | 9.24 %H20, 12.857 %CO2, 6.685 %O2, 289.1 Deg F | Results may be biased low due to matrix interference. RPD of >20% and spike recovery of 50% outside method limit of 85-115%.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0925 | 0.0001137 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 940740 | dscfm | 11.32 %H20, 12.795373822 %CO2, 6.37 %O2, 120.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0925 | 0.0001137 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 940740 | dscfm | 11.32 %H20, 12.795373822 %CO2, 6.37 %O2, 120.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0923 | 0.000103 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 948006 | dscfm | 11.33 %H20, 12.830598526 %CO2, 6.33 %O2, 120.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0923 | 0.0001223 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 948006 | dscfm | 11.33 %H20, 12.830598526 %CO2, 6.33 %O2, 120.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0988 | 0.0001212 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 949743 | dscfm | 11.45 %H20, 12.82179235 %CO2, 6.34 %O2, 120.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 1 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.108 | 0.0001331 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 949743 | dscfm | 11.45 %H20, 12.82179235 %CO2, 6.34 %O2, 120.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0672 | 7.683e-05 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 876652 | dscfm | 10.3 %H20, 12.936272639 %CO2, 6.21 %O2, 116.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0672 | 8.97e-05 | mg/Nm3 | Unknown | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 876652 | dscfm | 10.3 %H20, 12.936272639 %CO2, 6.21 %O2, 116.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0564 | 6.535e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 884700 | dscfm | 10.3 %H20, 12.751342942 %CO2, 6.42 %O2, 116.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0725 | 8.906e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 884700 | dscfm | 10.3 %H20, 12.751342942 %CO2, 6.42 %O2, 116.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0595 | 7.586e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 846533 | dscfm | 11.2 %H20, 12.680893533 %CO2, 6.5 %O2, 119.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 2 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 370 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0595 | 7.146e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 846533 | dscfm | 11.2 %H20, 12.680893533 %CO2, 6.5 %O2, 119.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0607 | 7.618e-05 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1211393 | dscfm | 16.5 %H20, 13.4 %CO2, 5.9 %O2, 126 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.045 | 5.687e-05 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1211393 | dscfm | 16.5 %H20, 13.4 %CO2, 5.9 %O2, 126 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.03 | 3.756e-05 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 1157212 | dscfm | 13.5 %H20, 13.7 %CO2, 5.4 %O2, 119 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.029 | 3.756e-05 | mg/Nm3 | Unknown | 2010-06-29 | Refer to sample method | U.S. EPA Method 30B | 1157212 | dscfm | 13.5 %H20, 13.7 %CO2, 5.4 %O2, 119 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0717 | 9.228e-05 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1255382 | dscfm | 13.8 %H20, 13.6 %CO2, 5.5 %O2, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 3 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0665 | 8.584e-05 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1255382 | dscfm | 13.8 %H20, 13.6 %CO2, 5.5 %O2, 120 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0631 | 8.047e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.3 %H20, 13.5 %CO2, 5.7 %O2, 116 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.0684 | 8.691e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.3 %H20, 13.5 %CO2, 5.7 %O2, 116 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0234 | 3.004e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.2 %H20, 13.5 %CO2, 5.7 %O2, 117 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.0249 | 3.219e-05 | mg/Nm3 | Unknown | 2010-05-19 | Refer to sample method | U.S. EPA Method 30B | 1042797 | dscfm | 12.2 %H20, 13.5 %CO2, 5.7 %O2, 117 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0164 | 2.146e-05 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1131652 | dscfm | 12.1 %H20, 13.5 %CO2, 5.5 %O2, 115 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | San Juan 2451_Unit 4 | NOx: Unspecified, PM: FFp, SO2: FGDw(Spray,Forced ox), Hg: ACSI | Coal-Fired Boilers | 544 |  | Public Service Company of New Mexico | subbituminous | Rocky Mountain | San Juan (NM) | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.0817 | 0.0001052 | mg/Nm3 | Unknown | 2010-05-20 | Refer to sample method | U.S. EPA Method 30B | 1131652 | dscfm | 12.1 %H20, 13.5 %CO2, 5.5 %O2, 115 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 2.73 | 0.003906 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B | 566768 | dscfm | 19.08 %H20, 15.8 %CO2, 3.76 %O2, 191 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 4.68 | 0.006728 | mg/Nm3 | Poor | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B | 582512 | dscfm | 17.55 %H20, 16.04 %CO2, 3.68 %O2, 192 Deg F | Spike recovery >115%; invalid run.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5A | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 3.83 | 0.005504 | mg/Nm3 | Unknown | 2010-03-03 | Refer to sample method | U.S. EPA Method 30B | 580652 | dscfm | 19.41 %H20, 16 %CO2, 3.67 %O2, 192 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 5.57 | 0.008176 | mg/Nm3 | Unknown | 2010-03-09 | Refer to sample method | U.S. EPA Method 30B | 579345 | dscfm | 19.67 %H20, 16.22 %CO2, 3.27 %O2, 192 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 6.31 | 0.00926 | mg/Nm3 | Poor | 2010-03-10 | Refer to sample method | U.S. EPA Method 30B | 563279 | dscfm | 20.47 %H20, 15.94 %CO2, 3.31 %O2, 194 Deg F | Spike recovery >115%; invalid run.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sandow Station 52071_5B | NOx: SNCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 282 |  | Sandow Generation Company LLC | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 4.92 | 0.007178 | mg/Nm3 | Poor | 2010-03-11 | Refer to sample method | U.S. EPA Method 30B | 580823 | dscfm | 19.76 %H20, 16.08 %CO2, 3.39 %O2, 193 Deg F | Spike recovery >115%; invalid run.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.11 | 0.0008509 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 1.51 | 0.001159 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.837 | 0.0006417 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 1 |  | 1.11 | 0.0008509 | mg/Nm3 | Unknown | 2010-03-04 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 2 |  | 1.51 | 0.001159 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scholz 642_Unit 2 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 49 |  | Gulf Power Company | bituminous | Eastern | WV | Wall-fired | Front wall-fired boiler. | 3 |  | 0.837 | 0.0006417 | mg/Nm3 | Unknown | 2010-03-05 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.0324 | 3.401e-05 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 242209 | dscfm | 4.9 %O2, 309 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0439 | 4.775e-05 | mg/Nm3 | Unknown | 2010-03-22 | Refer to sample method | U.S. EPA Method 30B | 247315 | dscfm | 5 %O2, 316 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Scrubgrass Generating Company L.P. 50974_Gen 1 | NOx: SNCR, PM: FFp, SO2: FGDcfb | Coal-Fired Boilers | 97 |  | Scrubgrass Generating Co. L.P. | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0296 | 3.155e-05 | mg/Nm3 | Unknown | 2010-03-23 | Refer to sample method | U.S. EPA Method 30B | 259777 | dscfm | 4.8 %O2, 305.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.00709 | 9.337e-06 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1327915 | dscfm | 11.37 %H20, 14.2 %CO2, 5.2 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.00602 | 7.833e-06 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1337687 | dscfm | 11.66 %H20, 14.3 %CO2, 5.2 %O2, 185 Deg F | Spiked trap invalid; results are only the unspiked trap
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-1 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.00642 | 7.956e-06 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1348413 | dscfm | 11.91 %H20, 14.5 %CO2, 5.9 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 1 |  | 0.00709 | 9.337e-06 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1327915 | dscfm | 11.37 %H20, 14.2 %CO2, 5.2 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 2 |  | 0.00602 | 7.833e-06 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1337687 | dscfm | 11.66 %H20, 14.3 %CO2, 5.2 %O2, 185 Deg F | Spiked trap invalid; results are only the unspiked trap
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Seward 3130_SEW-2 | NOx: SNCR, PM: PS FFp | Coal-Fired Boilers | 293 |  | RRI Energy Wholesale Generation LLC | waste unknown | Eastern | PA | Fluidized bed |  | 3 |  | 0.00642 | 7.956e-06 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1348413 | dscfm | 11.91 %H20, 14.5 %CO2, 5.9 %O2, 185 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 28 | 0.0296 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 28.5 | 0.03025 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW3-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 33.3 | 0.03538 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 1 |  | 28 | 0.0296 | mg/Nm3 | Unknown | 2010-06-07 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 2 |  | 28.5 | 0.03025 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Shawville 3131_SHAW4-1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 188 |  | RRI Energy Mid-Atlantic PH LLC | bituminous | Eastern | PA | Tangential |  | 3 |  | 33.3 | 0.03538 | mg/Nm3 | Unknown | 2010-06-09 | Not Specified | EPA method 29 |  |  |  | Analysis performed by method 6020 instead of 6010B; results may be biased.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 3.4 | 0.004822 | mg/Nm3 | Unknown | 2010-05-05 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 1.72 | 0.002578 | mg/Nm3 | Unknown | 2010-05-06 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results. Results biased low due to permanganate impinger being broken in transit to the lab.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 128 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 4.4 | 0.005915 | mg/Nm3 | Unknown | 2010-05-07 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 1 |  | 0.441 | 0.0005872 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 2 |  | 0.326 | 0.000434 | mg/Nm3 | Unknown | 2010-05-11 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sheldon Station 2277_U2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 141 |  | Nebraska Public Power District | subbituminous | Northern Great Plains | Powder River Basin | Cyclone |  | 3 |  | 0.225 | 0.0002672 | mg/Nm3 | Unknown | 2010-05-12 | Not Specified | EPA method 29 |  |  |  | Blank corrections were used to obtain final results.
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_1 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 55 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_2 | NOx: SNCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 51 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 1 |  | 1.48 | 0.0022 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 920926 | dscfm | 12.2 %H20, 16.1 %CO2, 3.4 %O2, 287 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 2 |  | 1.18 | 0.001738 | mg/Nm3 | Unknown | 2010-03-16 | Refer to sample method | U.S. EPA Method 30B | 868737 | dscfm | 12.7 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sibley 2094_3 | NOx: SCR, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 419 |  | KCP&L - Greater Missouri Operations Company | subbit/bit | Northern Great Plains, Rocky Mountain | Powder River Basin, Uinta (UT) | Cyclone |  | 3 |  | 1.23 | 0.001813 | mg/Nm3 | Unknown | 2010-03-17 | Refer to sample method | U.S. EPA Method 30B | 882744 | dscfm | 12.4 %H20, 16 %CO2, 3.3 %O2, 291 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.02 | 0.004964 | mg/Nm3 | Unknown | 2010-03-16 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 5.47 | 0.005368 | mg/Nm3 | Unknown | 2010-03-16 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Silver Bay Power 10849_GEN1 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 45 |  | Northshore Mining Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 4.8 | 0.004709 | mg/Nm3 | Unknown | 2010-03-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 1 |  | 1.45 | 0.001931 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 839000 | dscfm | 11.8 %H20, 14.3 %CO2, 4.6 %O2, 315 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 2 |  | 1.58 | 0.002114 | mg/Nm3 | Unknown | 2010-04-28 | Refer to sample method | U.S. EPA Method 30B | 839000 | dscfm | 11.8 %H20, 14.3 %CO2, 4.6 %O2, 315 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sioux 2107_002 | NOx: SNCR, PM: ESPc(With Conditioning), SO2: FGDw(Spray) | Coal-Fired Boilers | 524 |  | Union Electric Co. dba AmerenUE | subbit/bit | Northern Great Plains, Interior(East, No | Powder River Basin, IL | Cyclone |  | 3 |  | 1.29 | 0.001728 | mg/Nm3 | Unknown | 2010-05-03 | Refer to sample method | U.S. EPA Method 30B | 850000 | dscfm | 12 %H20, 14 %CO2, 4.5 %O2, 318 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 3.06 | 0.00353 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.4 %CO2, 9.5 %O2, 292.95 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 3.71 | 0.004292 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B |  |  | 11.3 %CO2, 9.6 %O2, 292.35 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B7 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 320 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 3.65 | 0.004217 | mg/Nm3 | Unknown | 2010-07-02 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.9 %CO2, 10 %O2, 300.45 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 4.56 | 0.005429 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 6.7 %O2, 292.45 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 4.58 | 0.005451 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.7 %O2, 288.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | South Oak Creek 4041_OCPP-B8 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 336 |  | Wisconsin Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.25 | 0.005022 | mg/Nm3 | Unknown | 2010-04-09 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.8 %O2, 289.95 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 1 |  | 0.436 | 0.0005276 | mg/Nm3 | Poor | 2010-04-26 | Refer to sample method | U.S. EPA Method 30B | 192592 | dscfm | 13.6899 %H20, 12.683 %CO2, 6.5 %O2, 189.52083333 Deg F | QC data outside method specified limits. High spike recovery
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 2 |  | 0.261 | 0.0003266 | mg/Nm3 | Poor | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 182619 | dscfm | 13.4 %H20, 13.1 %CO2, 6.1 %O2, 187.25 Deg F | QC data outside method specified limits. High spike recovery
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Southampton Power Station 10774_Unit 1 & 2 | NOx: Unspecified, PM: MC FFp, SO2: FGDsd | Coal-Fired Boilers | 68 |  | Virginia Electric & Power Company | bituminous | Eastern | KY, WV | Stoker | Spreader stoker boiler. | 3 |  | 0.142 | 0.0001788 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B | 184465 | dscfm | 13.7 %H20, 13.2 %CO2, 6 %O2, 186.20833333 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 2.97 | 0.003198 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 824382 | dscfm | 201.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 3.16 | 0.003401 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 829622 | dscfm | 202.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_3 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.18 | 0.003423 | mg/Nm3 | Unknown | 2010-02-27 | Refer to sample method | U.S. EPA Method 30B | 822115 | dscfm | 203.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 2.57 | 0.002768 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 859716 | dscfm | 15 %H20, 188.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 4.21 | 0.004528 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 854084 | dscfm | 15.1 %H20, %CO2, %O2, 189 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Springerville 8223_4 | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 450 |  | Jointly Owned | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 3.97 | 0.004271 | mg/Nm3 | Unknown | 2010-05-07 | Refer to sample method | U.S. EPA Method 30B | 846242 | dscfm | 15.3 %H20, %CO2, %O2, 189.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 1 |  | 0.00145 | 2.146e-06 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 159508 | dscfm | 12.54 %H20, 14.03 %CO2, 4.89 %O2, 191 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 2 |  | 0.00249 | 3.219e-06 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 156853 | dscfm | 12.53 %H20, 14.29 %CO2, 4.45 %O2, 193 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Spruance Genco, LLC 54081_GEN2 | NOx: Unspecified, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 29 |  | Spruance Genco, LLC | bituminous | Eastern | KY, WV | Stoker | Underfeed stoker boiler. | 3 |  | 0.00396 | 5.365e-06 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 159616 | dscfm | 12.63 %H20, 13.7 %CO2, 4.97 %O2, 195 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.705 | 0.0008852 | mg/Nm3 | Unknown | 2010-06-21 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.666 | 0.0008359 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Stanton Energy Center 564_2 coal | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw(Spray,Natural) | Coal-Fired Boilers | 468 |  | Orlando Utilities Commission | bituminous | Eastern | KY, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 0.474 | 0.0005955 | mg/Nm3 | Unknown | 2010-06-22 | Refer to sample method | U.S. EPA Method 30B
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 9.31 | 0.01025 | mg/Nm3 | Unknown | 2010-04-06 | Refer to sample method | U.S. EPA Method 30B | 453327 | dscfm | 11.47 %H20, 11.53 %CO2, 7.96 %O2, 321.7 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 9.39 | 0.01104 | mg/Nm3 | Unknown | 2010-04-07 | Refer to sample method | U.S. EPA Method 30B | 447069 | dscfm | 11.45 %H20, 12.32 %CO2, 7.35 %O2, 307.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | State Line 981_Unit 3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 216 |  | State Line Energy LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.42 | 0.005183 | mg/Nm3 | Unknown | 2010-04-08 | Refer to sample method | U.S. EPA Method 30B | 443559 | dscfm | 11.32 %H20, 12.29 %CO2, 7.2 %O2, 308.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 1 |  | 2.8 | 0.002859 | mg/Nm3 | Unknown | 2010-08-10 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.15 %O2, 291.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 2 |  | 3.52 | 0.003681 | mg/Nm3 | Unknown | 2010-08-11 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.07 %O2, 295.33 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunbury Generation LP 3152_Boiler 4 | NOx: Unspecified, PM: ESPc(With Conditioning) | Coal-Fired Boilers | 128 |  | Sunbury Generation LP | bituminous | Eastern | PA | Wall-fired | Front wall-fired boiler. | 3 |  | 2.37 | 0.002477 | mg/Nm3 | Unknown | 2010-08-12 | Refer to sample method | U.S. EPA Method 30B |  |  | 8.11 %O2, 286.31 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 1 |  | 0.0421 | 5.848e-05 | mg/Nm3 | Unknown | 2010-06-21 | Refer to sample method | U.S. EPA Method 30B | 151955 | dscfm | 8.87 %H20, 15.3 %CO2, 4.3 %O2, 315 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 2 |  | 0.0623 | 8.648e-05 | mg/Nm3 | Unknown | 2010-06-23 | Refer to sample method | U.S. EPA Method 30B | 153420 | dscfm | 11.9 %H20, 15.6 %CO2, 4.3 %O2, 316 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Sunnyside Cogen Associates 50951_Config 1 | NOx: Unspecified, PM: FFp, SO2: FGDw | Coal-Fired Boilers | 60 |  | Sunnyside Cogeneration Associates | waste unknown | Eastern | Unknown | Fluidized bed |  | 3 |  | 0.0789 | 0.0001094 | mg/Nm3 | Unknown | 2010-06-24 | Refer to sample method | U.S. EPA Method 30B | 152310 | dscfm | 11.6 %H20, 14.9 %CO2, 4.5 %O2, 315 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 5.83 | 0.00831 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 6.52 | 0.01025 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC1 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 83 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 4.8 | 0.007498 | mg/Nm3 | Unknown | 2010-05-19 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 2.49 | 0.003437 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 3.42 | 0.0047 | mg/Nm3 | Unknown | 2010-05-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Taconite Harbor Energy Center 10075_THEC2 | NOx: SNCR, PM: ESPc(Without Conditioning), SO3: SI | Coal-Fired Boilers | 79 |  | Allete, Inc d/b/a Minnesota Power | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 2.69 | 0.004139 | mg/Nm3 | Unknown | 2010-05-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 2 |  | 0.465 | 0.0006223 | mg/Nm3 | Unknown | 2010-05-25 | Refer to sample method | U.S. EPA Method 30B | 1121239 | dscfm | 10 %H20, 14.2 %CO2, 5 %O2, 312.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 4 |  | 0.682 | 0.000912 | mg/Nm3 | Unknown | 2010-05-26 | Refer to sample method | U.S. EPA Method 30B | 1119227 | dscfm | 11.6 %H20, 14.3 %CO2, 4.8 %O2, 313.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Tanners Creek 988_TC-4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 579 |  | Indiana Michigan Power Company | subbit/bit | Northern Great Plains, Eastern | Powder River Basin, PA, WV | Cyclone |  | 5 |  | 1.17 | 0.001567 | mg/Nm3 | Unknown | 2010-05-28 | Refer to sample method | U.S. EPA Method 30B | 1111682 | dscfm | 11.1 %H20, 14 %CO2, 5.2 %O2, 307.9 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1.23 | 0.001322 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 484727 | dscfm | 14.18 %H20, 13 %CO2, 5.98 %O2, 191 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1.27 | 0.001347 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 483967 | dscfm | 14.18 %H20, 13 %CO2, 6.15 %O2, 191 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.28 | 0.001361 | mg/Nm3 | Unknown | 2010-06-19 | Refer to sample method | U.S. EPA Method 30B | 482783 | dscfm | 14.17 %H20, 13.6 %CO2, 6.2 %O2, 191 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.991 | 0.001221 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.671 | 0.0008502 | mg/Nm3 | Unknown | 2010-06-17 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | TS Power Plant 56224_TSPower | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 242 |  | Newmont Nevada Energy Investment LLC | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.05 | 0.001319 | mg/Nm3 | Unknown | 2010-06-18 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 1 |  | 10.1 | 0.01343 | mg/Nm3 | Unknown | 2010-04-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 2 |  | 7.16 | 0.01035 | mg/Nm3 | Unknown | 2010-04-22 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Twin Oaks Power One 7030_U2 | NOx: Unspecified, PM: FFr | Coal-Fired Boilers | 172 |  | Optim Energy Twin Oaks, LP | lignite | Gulf | TX | Fluidized bed |  | 3 |  | 3.4 | 0.005035 | mg/Nm3 | Unknown | 2010-04-23 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 1 |  | 4.51 | 0.005483 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 2 |  | 6.86 | 0.00833 | mg/Nm3 | Unknown | 2010-07-20 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Urquhart 3295_URQ003 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 103 |  | South Carolina Electric & Gas | bituminous | Eastern | KY, TN | Tangential |  | 3 |  | 5.06 | 0.006128 | mg/Nm3 | Unknown | 2010-07-21 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0157 | 1.931e-05 | mg/Nm3 | Unknown | 2010-07-19 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.675 %CO2, 10.225 %O2, 332.075 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.0231 | 2.897e-05 | mg/Nm3 | Unknown | 2010-07-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.225 %CO2, 10.675 %O2, 322.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B1 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0191 | 2.361e-05 | mg/Nm3 | Unknown | 2010-07-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 10.3 %CO2, 10.6 %O2, 322.65 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0382 | 4.292e-05 | mg/Nm3 | Unknown | 2010-03-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.2 %O2, 303.05 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0194 | 2.146e-05 | mg/Nm3 | Unknown | 2010-03-31 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.2 %O2, 307.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B2 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0246 | 3.219e-05 | mg/Nm3 | Unknown | 2010-04-01 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 6.3 %O2, 311.15 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.031 | 4.292e-05 | mg/Nm3 | Unknown | 2010-04-20 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.8 %CO2, 5.9 %O2, 314.725 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 2 |  | 0.019 | 2.146e-05 | mg/Nm3 | Unknown | 2010-04-21 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.5 %CO2, 6 %O2, 311.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B3 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0128 | 1.073e-05 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 5.9 %O2, 312.05 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 1 |  | 0.0729 | 8.584e-05 | mg/Nm3 | Unknown | 2010-04-27 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.3 %CO2, 6.2 %O2, 311.2 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 3 |  | 0.0491 | 6.438e-05 | mg/Nm3 | Unknown | 2010-04-29 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.6 %CO2, 5.9 %O2, 316.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Valley 4042_VAPP-B4 | NOx: Unspecified, PM: FFp | Coal-Fired Boilers | 72 |  | Wisconsin Electric Power Company | bituminous | Rocky Mountain | Green River (CO) | Wall-fired | Front wall-fired boiler. | 4 |  | 0.0982 | 0.0001288 | mg/Nm3 | Unknown | 2010-04-30 | Refer to sample method | U.S. EPA Method 30B |  |  | 12.7 %CO2, 5.7 %O2, 319.85 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 72 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_001 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 72 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.47 | 0.0006052 | mg/Nm3 | Unknown | 2010-08-22 | Refer to sample method | U.S. EPA Method 30B | 483546 | dscfm | 11.5 %H20, 12 %CO2, 6 %O2, 348 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Vermilion 897_002 | NOx: Unspecified, PM: ESPc(Without Conditioning) FFp, Hg: ACSI | Coal-Fired Boilers | 110 |  | Dynegy Midwest Generation Inc. | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.324 | 0.0004142 | mg/Nm3 | Unknown | 2010-08-23 | Refer to sample method | U.S. EPA Method 30B | 491813 | dscfm | 12.2 %H20, 12 %CO2, 6 %O2, 345.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 1 |  | 0.865 | 0.001014 | mg/Nm3 | Unknown | 2010-04-22 | Refer to sample method | U.S. EPA Method 30B | 3369921 | dscfm | 13.1 %H20, 12.26 %CO2, 6.96 %O2, 127 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 2 |  | 1.4 | 0.001641 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3341205 | dscfm | 15 %H20, 12.23 %CO2, 6.93 %O2, 128 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W H Zimmer 6019_1 | NOx: SCR, PM: ESPc(Without Conditioning), SO2: FGDw, SO3: SI | Coal-Fired Boilers | 1408 |  | Duke Energy Ohio | bituminous | Interior(East, North), Eastern | IL, IN, OH, WV | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.19 | 0.001399 | mg/Nm3 | Unknown | 2010-04-23 | Refer to sample method | U.S. EPA Method 30B | 3346156 | dscfm | 14.9 %H20, 12.31 %CO2, 6.94 %O2, 129 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 1 |  | 5.25 | 0.004367 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 182545 | dscfm | 5.9 %H20, %CO2, %O2, 222 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 2 |  | 6.25 | 0.005204 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 186229 | dscfm | 6.3 %H20, %CO2, %O2, 213 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | W.H. Weatherspoon Plant 2716_Wea_Cfg_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 53 |  | Progress Energy Carolinas, Inc. | bituminous | Eastern | KY, WV | Wall-fired | Front wall-fired boiler. | 3 |  | 3.94 | 0.003283 | mg/Nm3 | Unknown | 2010-02-16 | Refer to sample method | U.S. EPA Method 30B | 188034 | dscfm | 5.8 %H20, %CO2, %O2, 216 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 1 |  | 6.5 | 0.007428 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1163199 | dscfm | 9 %H20, 11.5 %CO2, 7.3 %O2, 265.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 2 |  | 6.31 | 0.007169 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1204758 | dscfm | 8.75 %H20, 11.4 %CO2, 7.4 %O2, 275.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_4 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 90 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Wall-fired | Front wall-fired boiler. | 3 |  | 6.32 | 0.007329 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1255300 | dscfm | 8.81 %H20, 11.9 %CO2, 7.1 %O2, 270.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 1 |  | 6.5 | 0.007428 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1163199 | dscfm | 9 %H20, 11.5 %CO2, 7.3 %O2, 265.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 2 |  | 6.31 | 0.007169 | mg/Nm3 | Unknown | 2010-06-09 | Refer to sample method | U.S. EPA Method 30B | 1204758 | dscfm | 8.75 %H20, 11.4 %CO2, 7.4 %O2, 275.1 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wabash River 1010_6 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 342 |  | Duke Energy Indiana, Inc. | bituminous | Interior(East, North) | IN | Tangential |  | 3 |  | 6.32 | 0.007329 | mg/Nm3 | Unknown | 2010-06-10 | Refer to sample method | U.S. EPA Method 30B | 1255300 | dscfm | 8.81 %H20, 11.9 %CO2, 7.1 %O2, 270.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 1 |  | 2.97 | 0.003848 | mg/Nm3 | Unknown | 2010-04-06 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 2 |  | 3.05 | 0.00388 | mg/Nm3 | Unknown | 2010-04-07 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Walter Scott Jr. Energy Center Walter Scott Jr. Energy Center 1082_4 | NOx: SCR, PM: FFp, SO2: FGDcfb, Hg: ACSI | Coal-Fired Boilers | 850 |  | MidAmerican Energy Company, Alta Municipal Utilities | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired |  | 3 |  | 2.79 | 0.00355 | mg/Nm3 | Unknown | 2010-04-08 | Not Specified | EPA method 29
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 0.369 | 0.0004077 | mg/Nm3 | Unknown | 2010-07-13 | Refer to sample method | U.S. EPA Method 30B | 807877 | dscfm | 12.1 %H20, 13.07 %CO2, 6.5 %O2, 338 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.347 | 0.0003863 | mg/Nm3 | Unknown | 2010-07-14 | Refer to sample method | U.S. EPA Method 30B | 780068 | dscfm | 12.6 %H20, 13.23 %CO2, 6.2 %O2, 340.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Waukegan 883_WK8CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 383 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.391 | 0.0004399 | mg/Nm3 | Unknown | 2010-07-15 | Refer to sample method | U.S. EPA Method 30B | 798069 | dscfm | 12.9 %H20, 13.43 %CO2, 6 %O2, 348.8 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 5.18 | 0.006213 | mg/Nm3 | Unknown | 2010-04-13 | Refer to sample method | U.S. EPA Method 30B | 1437736 | dscfm | 10.2 %H20, 12.7 %CO2, 6.8 %O2, 306.3 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 5.38 | 0.006138 | mg/Nm3 | Unknown | 2010-04-14 | Refer to sample method | U.S. EPA Method 30B | 1513081 | dscfm | 11 %H20, 12.4 %CO2, 7.3 %O2, 299.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Welsh 6139_WE-1 | NOx: Unspecified, PM: ESPh(Without Conditioning) | Coal-Fired Boilers | 558 |  | Southwestern Electric Power Company | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 5.2 | 0.006052 | mg/Nm3 | Unknown | 2010-04-15 | Refer to sample method | U.S. EPA Method 30B | 1517114 | dscfm | 10.8 %H20, 12.8 %CO2, 6.8 %O2, 298.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.38 | 0.001856 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 769000 | dscfm | 11.2 %H20, 13.8 %CO2, 5.3 %O2, 325 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 0.956 | 0.001298 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 795000 | dscfm | 11.2 %H20, 14.1 %CO2, 5.1 %O2, 314 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W3 | NOx: Unspecified, PM: FFp, Hg: ACSI | Coal-Fired Boilers | 366 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 0.638 | 0.0008723 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 769000 | dscfm | 11.2 %H20, 14.2 %CO2, 5 %O2, 310 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 1 |  | 1.08 | 0.001459 | mg/Nm3 | Unknown | 2010-05-11 | Refer to sample method | U.S. EPA Method 30B | 1130576 | dscfm | 15.6 %H20, 13.8 %CO2, 5.51 %O2, 175.75 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 2 |  | 0.839 | 0.001105 | mg/Nm3 | Unknown | 2010-05-12 | Refer to sample method | U.S. EPA Method 30B | 1132600 | dscfm | 15.7 %H20, 13.73 %CO2, 5.75 %O2, 178.87 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Weston 4078_W4 | NOx: SCR, PM: FFp, SO2: FGDsd, Hg: ACSI | Coal-Fired Boilers | 575 |  | Wisconsin Public Service Corporation | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Opposed wall-fired boiler. | 3 |  | 1.31 | 0.001719 | mg/Nm3 | Unknown | 2010-05-13 | Refer to sample method | U.S. EPA Method 30B | 1127753 | dscfm | 16 %H20, 13.76 %CO2, 5.57 %O2, 178.12 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 8.87 | 0.01073 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 197956 | dscfm | 11.8 %H20, 13.8 %CO2, 6.16 %O2, 327 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 9.45 | 0.01148 | mg/Nm3 | Unknown | 2010-03-24 | Refer to sample method | U.S. EPA Method 30B | 197944 | dscfm | 11.8 %H20, 13.8 %CO2, 6.16 %O2, 327 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Whelan Energy Center Unit 1 (WEC1) 60_1 | NOx: Unspecified, PM: ESPc(Without Conditioning) | Coal-Fired Boilers | 84 |  | Hastings Utilities / City of Hastings, NE | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 7.98 | 0.009743 | mg/Nm3 | Unknown | 2010-03-25 | Refer to sample method | U.S. EPA Method 30B | 200131 | dscfm | 11.9 %H20, 13.9 %CO2, 6.08 %O2, 315 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 1 |  | 1.04 | 0.001373 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 1002207 | dscfm | 11.4 %H20, 14.3 %CO2, 5.3 %O2, 308.6 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 2 |  | 1.18 | 0.001567 | mg/Nm3 | Unknown | 2010-07-01 | Refer to sample method | U.S. EPA Method 30B | 1007312 | dscfm | 10.4 %H20, 14.5 %CO2, 5.1 %O2, 311.4 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Will County 884_WC4CONFIG | NOx: Unspecified, PM: ESPc(Without Conditioning), Hg: ACSI | Coal-Fired Boilers | 542 |  | Midwest Generation, LLC | subbituminous | Northern Great Plains | Powder River Basin | Tangential |  | 3 |  | 1.25 | 0.001652 | mg/Nm3 | Unknown | 2010-07-02 | Refer to sample method | U.S. EPA Method 30B | 972834 | dscfm | 11.8 %H20, 14.2 %CO2, 5.2 %O2, 311.5 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 4.26 | 0.005633 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 238050 | dscfm | 15.1 %H20, 15.5 %CO2, 3.8 %O2, 184 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 1 55479_WYG1Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 91 |  | Black Hills Wyoming, Inc | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 5.06 | 0.006299 | mg/Nm3 | Unknown | 2010-06-30 | Refer to sample method | U.S. EPA Method 30B | 223103 | dscfm | 17.3 %H20, 15.7 %CO2, 3.7 %O2, 186 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 1 |  | 5.38 | 0.007436 | mg/Nm3 | Unknown | 2010-05-04 | Refer to sample method | U.S. EPA Method 30B | 248616 | dscfm | 15.1 %H20, 15.3 %CO2, 4.4 %O2, 182 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 2 |  | 6.03 | 0.008326 | mg/Nm3 | Unknown | 2010-05-05 | Refer to sample method | U.S. EPA Method 30B | 240230 | dscfm | 16.5 %H20, 14.4 %CO2, 4.4 %O2, 180 Deg F
XX-IC-2010 | 2010 Utility HAPs Information Collection Request | Wygen 2 56319_WYG2Cfg | NOx: SCR, PM: FFp, SO2: FGDsd | Coal-Fired Boilers | 96 |  | Cheyenne Light, Fuel & Power | subbituminous | Northern Great Plains | Powder River Basin | Wall-fired | Front wall-fired boiler. | 3 |  | 6.33 | 0.008745 | mg/Nm3 | Unknown | 2010-05-06 | Refer to sample method | U.S. EPA Method 30B | 227964 | dscfm | 17.1 %H20, 15 %CO2, 4.4 %O2, 180 Deg F